## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-06-01 | 103210 | 103.21 | 7.01 | 7.25 | 130 | 25 | 328 | 42 | 298 | 36 | NA | 600 | 0.2 | 25.3 | 1200000
2023-06-02 | 107390 | 107.39 | 6.97 | 7.23 | 140 | 26 | 324 | 40 | 305 | 35 | NA | 700 | 0.3 | 24.9 | 1300000
2023-06-03 | 105520 | 105.52 | 7.18 | 7.28 | 130 | 25 | 320 | 42 | 297 | 36 | NA | 400 | 0.3 | 25.1 | 1200000
2023-06-04 | 101860 | 101.86 | 7 | 7.17 | 125 | 24 | 332 | 41 | 297 | 35 | NA | 400 | 0.2 | 24.8 | 1100000
2023-06-05 | 105790 | 105.79 | 7.28 | 7.18 | 135 | 26 | 330 | 44 | 304 | 33 | NA | 800 | 0.3 | 24.7 | 1700000
2023-06-06 | 96520 | 96.52 | 7.26 | 7.23 | 145 | 25 | 326 | 40 | 307 | 34 | NA | 600 | 0.2 | 24.8 | 1300000
2023-06-07 | 101060 | 101.05 | 7.07 | 7.17 | 130 | 24 | 330 | 43 | 290 | 36 | NA | 500 | 0.3 | 24.86 | 1400000
2023-06-08 | 108510 | 108.51 | 7.01 | 7.15 | 125 | 25 | 335 | 44 | 298 | 35 | NA | 700 | 0.2 | 25.02 | 1700000
2023-06-09 | 108380 | 108.38 | 7.11 | 7.55 | 130 | 24 | 324 | 40 | 295 | 34 | NA | 400 | 0.2 | 24.65 | 1200000
2023-06-10 | 101150 | 101.15 | 7.02 | 7.62 | 125 | 25 | 316 | 44 | 291 | 36 | NA | 600 | 0.3 | 25.05 | 1400000
2023-06-11 | 97220 | 97.22 | 7.03 | 7.64 | 130 | 23 | 326 | 44 | 304 | 34 | NA | 500 | 0.2 | 25.1 | 1300000
2023-06-12 | 97470 | 97.47 | 7.05 | 8.06 | 130 | 24 | 330 | 43 | 301 | 36 | NA | 800 | 0.3 | 24.79 | 1700000
2023-06-13 | 101700 | 101.7 | 7.1 | 7.67 | 135 | 24 | 324 | 40 | 298 | 35 | NA | 600 | 0.3 | 24.53 | 1400000
2023-06-14 | 99400 | 99.4 | 7.06 | 7.64 | 130 | 25 | 334 | 42 | 299 | 34 | NA | 500 | 0.2 | 24.7 | 1200000
2023-06-15 | 102060 | 102.06 | 7.09 | 7.58 | 125 | 23 | 324 | 40 | 295 | 32 | NA | 700 | 0.3 | 24.32 | 1400000
2023-06-16 | 104760 | 104.56 | 7.03 | 8.05 | 120 | 24 | 312 | 44 | 288 | 37 | NA | 800 | 0.2 | 25.09 | 1700000
2023-06-17 | 102070 | 102.07 | 7.18 | 7.76 | 125 | 26 | 330 | 46 | 302 | 36 | NA | 600 | 0.3 | 24.7 | 1100000
2023-06-18 | 101040 | 101.04 | 7.01 | 7.62 | 130 | 25 | 326 | 38 | 294 | 33 | NA | 800 | 0.3 | 25.07 | 1200000
2023-06-19 | 99510 | 99.51 | 7.04 | 7.58 | 125 | 24 | 320 | 40 | 289 | 32 | NA | 500 | 0.2 | 24.6 | 1400000
2023-06-20 | 101750 | 101.75 | 7.14 | 7.53 | 130 | 29 | 332 | 48 | 308 | 45 | NA | 600 | 0.3 | 24.5 | 1100000
2023-06-21 | 103410 | 103.41 | 7.06 | 7.68 | 135 | 25 | 324 | 40 | 300 | 35 | NA | 500 | 0.2 | 24.61 | 1300000
2023-06-22 | 107270 | 107.27 | 7.12 | 7.82 | 125 | 24 | 320 | 44 | 295 | 38 | NA | 700 | 0.3 | 24.29 | 1400000
2023-06-23 | 106570 | 106.57 | 7.2 | 7.85 | 130 | 25 | 326 | 40 | 305 | 34 | NA | 800 | 0.2 | 25.03 | 1200000
2023-06-24 | 88150 | 88.15 | 7.23 | 7.74 | 140 | 24 | 330 | 36 | 310 | 36 | NA | 700 | 0.2 | 24.8 | 1400000
2023-06-25 | 97550 | 97.55 | 7.05 | 7.48 | 135 | 24 | 326 | 40 | 302 | 33 | NA | 600 | 0.3 | 25.1 | 1700000
2023-06-26 | 102220 | 102.01 | 7.01 | 7.19 | 120 | 23 | 320 | 38 | 295 | 31 | NA | 500 | 0.2 | 24.8 | 1300000
2023-06-27 | 104220 | 104.22 | 7.15 | 7.88 | 120 | 28 | 328 | 42 | 304 | 37 | NA | 400 | 0.3 | 25 | 1100000
2023-06-28 | 109500 | 109.5 | 7.33 | 7.51 | 130 | 24 | 320 | 40 | 322 | 33 | NA | 600 | 0.2 | 24.88 | 1400000
2023-06-29 | 117340 | 117.34 | 7.64 | 7.48 | 120 | 25 | 348 | 41 | 326 | 31 | NA | 700 | 0.3 | 24.3 | 1300000
2023-06-30 | 129540 | 129.54 | 7.22 | 7.43 | 125 | 26 | 332 | 40 | 315 | 30 | NA | 800 | 0.2 | 23.59 | 1200000
Average | 103738 | 103.724 | 7.1217 | 7.534 | 129.1667 | 24.8 | 326.5667 | 41.5333 | 301.1333 | 34.7333 | NA | 613.3333 | 0.25 | 24.766 | 1343333.3333
3111.72
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 88150 | 88.15 | 6.97 | 7.15 | 120 | 23 | 312 | 36 | 288 | 30 |  | 400 | 0.2 | 23.59 | 1100000
Max | 129540 | 129.54 | 7.64 | 8.06 | 145 | 29 | 348 | 48 | 326 | 45 |  | 800 | 0.3 | 25.3 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-06-01 | 68410 | 68.41 | 7.35 | 7.74 | 135 | 16 | 316 | 40 | 298 | 27 | NA | 400 | 0.3 | 24.98 | 1400000
2023-06-02 | 69610 | 69.61 | 7.31 | 7.75 | 130 | 17 | 336 | 44 | 293 | 26 | NA | 600 | 0.2 | 23.16 | 1700000
2023-06-03 | 71200 | 71.2 | 7.34 | 7.78 | 140 | 18 | 328 | 44 | 288 | 27 | NA | 700 | 0.3 | 22.18 | 1400000
2023-06-04 | 65790 | 65.97 | 7.37 | 7.79 | 125 | 16 | 324 | 40 | 295 | 28 | NA | 500 | 0.2 | 23.57 | 1300000
2023-06-05 | 70410 | 70.41 | 7.29 | 7.8 | 130 | 17 | 332 | 44 | 302 | 26 | NA | 400 | 0.3 | 22.63 | 1400000
2023-06-06 | 71450 | 71.45 | 7.35 | 7.78 | 135 | 16 | 324 | 40 | 289 | 27 | NA | 600 | 0.3 | 23.93 | 1700000
2023-06-07 | 70100 | 70.1 | 7.24 | 7.76 | 125 | 17 | 320 | 44 | 282 | 28 | NA | 700 | 0.2 | 24.33 | 1400000
2023-06-08 | 68220 | 68.22 | 7.27 | 7.79 | 140 | 18 | 340 | 48 | 308 | 27 | NA | 500 | 0.3 | 23.37 | 1300000
2023-06-09 | 67920 | 67.92 | 7.37 | 7.77 | 130 | 16 | 328 | 40 | 289 | 26 | NA | 600 | 0.2 | 24.74 | 1400000
2023-06-10 | 64480 | 64.48 | 7.36 | 7.78 | 135 | 17 | 332 | 44 | 297 | 28 | NA | 400 | 0.3 | 23.68 | 1700000
2023-06-11 | 75430 | 75.43 | 7.15 | 7.71 | 125 | 16 | 312 | 40 | 275 | 27 | NA | 700 | 0.2 | 24.19 | 1300000
2023-06-12 | 73560 | 73.56 | 7.18 | 7.75 | 135 | 18 | 308 | 44 | 291 | 28 | NA | 500 | 0.3 | 23.54 | 1400000
2023-06-13 | 69890 | 69.89 | 7.28 | 7.79 | 125 | 16 | 316 | 40 | 295 | 27 | NA | 600 | 0.3 | 23.97 | 1700000
2023-06-14 | 74730 | 74.73 | 7.31 | 7.8 | 130 | 17 | 324 | 44 | 283 | 26 | NA | 400 | 0.2 | 23.36 | 1300000
2023-06-15 | 69750 | 69.75 | 7.33 | 7.81 | 140 | 18 | 328 | 44 | 287 | 27 | NA | 700 | 0.3 | 24.35 | 1400000
2023-06-16 | 72230 | 72.23 | 7.26 | 7.8 | 135 | 17 | 312 | 40 | 292 | 28 | NA | 500 | 0.3 | 22.97 | 1700000
2023-06-17 | 69530 | 69.53 | 7.15 | 7.78 | 130 | 18 | 332 | 48 | 306 | 27 | NA | 600 | 0.2 | 23.46 | 1300000
2023-06-18 | 71580 | 71.58 | 7.12 | 7.76 | 125 | 16 | 308 | 40 | 275 | 26 | NA | 400 | 0.2 | 24.17 | 1400000
2023-06-19 | 71150 | 71.15 | 7.23 | 7.79 | 135 | 17 | 324 | 44 | 293 | 28 | NA | 600 | 0.3 | 23.37 | 1700000
2023-06-20 | 69810 | 69.81 | 7.25 | 7.74 | 140 | 18 | 316 | 40 | 285 | 26 | NA | 500 | 0.3 | 22.8 | 1300000
2023-06-21 | 77720 | 77.72 | 7.17 | 7.77 | 130 | 16 | 332 | 44 | 302 | 28 | NA | 600 | 0.2 | 23.49 | 1400000
2023-06-22 | 84110 | 84.11 | 7.12 | 7.74 | 135 | 15 | 324 | 40 | 285 | 27 | NA | 700 | 0.3 | 23.13 | 1700000
2023-06-23 | 80820 | 80.82 | 7.16 | 7.73 | 125 | 17 | 312 | 44 | 287 | 26 | NA | 600 | 0.3 | 23.56 | 1300000
2023-06-24 | 77500 | 77.5 | 7.14 | 7.69 | 130 | 16 | 316 | 40 | 283 | 25 | NA | 500 | 0.2 | 23.42 | 1400000
2023-06-25 | 75840 | 75.84 | 7.12 | 7.7 | 135 | 17 | 328 | 44 | 278 | 27 | NA | 700 | 0.3 | 24.68 | 1300000
2023-06-26 | 77140 | 77.14 | 7.09 | 7.69 | 130 | 16 | 312 | 40 | 273 | 26 | NA | 600 | 0.2 | 23.11 | 1700000
2023-06-27 | 77610 | 77.61 | 7.03 | 7.73 | 125 | 17 | 308 | 40 | 254 | 25 | NA | 500 | 0.3 | 22.41 | 1200000
2023-06-28 | 82110 | 82.11 | 7.12 | 7.71 | 120 | 16 | 312 | 44 | 285 | 27 | NA | 400 | 0.2 | 23.44 | 1300000
2023-06-29 | 87130 | 87.13 | 7.06 | 7.67 | 125 | 17 | 308 | 40 | 274 | 26 | NA | 600 | 0.3 | 23.25 | 1700000
2023-06-30 | 91380 | 91.41 | 7.02 | 7.65 | 130 | 18 | 320 | 44 | 295 | 28 | NA | 500 | 0.2 | 24.49 | 1400000
Average | 73887 | 73.894 | 7.218 | 7.7517 | 131 | 16.8 | 321.0667 | 42.4 | 287.9667 | 26.8333 | NA | 553.3333 | 0.25667 | 23.591 | 1453333.3333
2216.82
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 64480 | 64.48 | 7.02 | 7.65 | 120 | 15 | 308 | 40 | 254 | 25 |  | 400 | 0.2 | 22.18 | 1200000
Max | 91380 | 91.41 | 7.37 | 7.81 | 140 | 18 | 340 | 48 | 308 | 28 |  | 700 | 0.3 | 24.98 | 1700000