## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-06-01 | 105950 | 105.95 | 7.19 | 7.48 | 140 | 20 | 308 | 44 | 273 | 36 | NA | 500 | 0.3 | 23.31 | 1300000
2024-06-02 | 102260 | 102.26 | 7.28 | 7.56 | 135 | 22 | 296 | 48 | 265 | 38 | NA | 700 | 0.3 | 23.03 | 1700000
2024-06-03 | 101010 | 101.01 | 7.25 | 7.53 | 130 | 19 | 304 | 44 | 268 | 33 | NA | 600 | 0.3 | 23.25 | 1400000
2024-06-04 | 100250 | 100.25 | 7.19 | 7.55 | 135 | 21 | 308 | 40 | 260 | 35 | NA | 400 | 0.3 | 23.17 | 1200000
2024-06-05 | 99350 | 99.35 | 7.23 | 7.57 | 130 | 23 | 292 | 48 | 275 | 32 | NA | 500 | 0.3 | 23.65 | 1700000
2024-06-06 | 106900 | 106.9 | 7.24 | 7.62 | 125 | 18 | 308 | 40 | 269 | 34 | NA | 600 | 0.3 | 23.16 | 1100000
2024-06-07 | 108070 | 108.07 | 7.27 | 7.66 | 135 | 22 | 304 | 48 | 273 | 33 | NA | 700 | 0.3 | 23.15 | 1300000
2024-06-08 | 108610 | 108.61 | 7.23 | 7.44 | 140 | 20 | 300 | 44 | 265 | 35 | NA | 400 | 0.3 | 22.91 | 1700000
2024-06-09 | 108310 | 108.31 | 7.25 | 7.43 | 130 | 19 | 296 | 40 | 273 | 32 | NA | 500 | 0.3 | 23.14 | 1200000
2024-06-10 | 108380 | 108.38 | 7.15 | 7.38 | 125 | 23 | 312 | 48 | 277 | 36 | NA | 600 | 0.3 | 22.28 | 1400000
2024-06-11 | 106900 | 106.9 | 7.11 | 7.33 | 140 | 21 | 316 | 44 | 267 | 34 | NA | 700 | 0.3 | 23.05 | 1100000
2024-06-12 | 104430 | 104.43 | 7.17 | 7.35 | 135 | 19 | 308 | 40 | 270 | 35 | NA | 400 | 0.3 | 22.54 | 1300000
2024-06-13 | 102170 | 102.17 | 7.19 | 7.36 | 130 | 18 | 304 | 44 | 277 | 37 | NA | 500 | 0.3 | 23.09 | 1200000
2024-06-14 | 105170 | 105.17 | 7.17 | 7.25 | 135 | 20 | 300 | 40 | 278 | 34 | NA | 600 | 0.3 | 23.12 | 1700000
2024-06-15 | 100310 | 100.31 | 7.15 | 7.28 | 140 | 22 | 308 | 44 | 275 | 36 | NA | 700 | 0.3 | 23.74 | 1400000
2024-06-16 | 92420 | 92.42 | 7.19 | 7.24 | 130 | 20 | 308 | 40 | 282 | 38 | NA | 400 | 0.3 | 23.1 | 1200000
2024-06-17 | 100110 | 100.11 | 7.18 | 7.32 | 125 | 21 | 296 | 44 | 273 | 35 | NA | 500 | 0.3 | 23.04 | 1100000
2024-06-18 | 90180 | 90.18 | 7.21 | 7.38 | 135 | 22 | 312 | 48 | 265 | 38 | NA | 700 | 0.3 | 23.51 | 1300000
2024-06-19 | 90310 | 90.31 | 7.16 | 7.24 | 130 | 23 | 312 | 44 | 277 | 34 | NA | 600 | 0.3 | 23.08 | 1700000
2024-06-20 | 101190 | 101.19 | 7.21 | 7.28 | 140 | 24 | 316 | 48 | 282 | 37 | NA | 400 | 0.3 | 23.44 | 1200000
2024-06-21 | 99510 | 99.51 | 7.19 | 7.27 | 130 | 20 | 300 | 44 | 274 | 35 | NA | 500 | 0.3 | 23.4 | 1300000
2024-06-22 | 92710 | 92.71 | 7.16 | 7.29 | 135 | 21 | 296 | 40 | 271 | 34 | NA | 700 | 0.3 | 23.08 | 1400000
2024-06-23 | 95780 | 95.78 | 7.22 | 7.34 | 130 | 20 | 304 | 44 | 265 | 37 | NA | 600 | 0.3 | 22.18 | 1100000
2024-06-24 | 98180 | 98.18 | 7.23 | 7.36 | 125 | 19 | 292 | 40 | 275 | 33 | NA | 400 | 0.3 | 23.26 | 1700000
2024-06-25 | 98070 | 98.07 | 7.18 | 7.32 | 135 | 21 | 308 | 44 | 268 | 32 | NA | 500 | 0.3 | 23.12 | 1200000
2024-06-26 | 105940 | 105.94 | 7.16 | 7.28 | 140 | 22 | 312 | 40 | 281 | 31 | NA | 700 | 0.3 | 23.14 | 1100000
2024-06-27 | 89860 | 89.86 | 7.21 | 7.36 | 130 | 20 | 300 | 44 | 276 | 33 | NA | 700 | 0.3 | 23.08 | 1400000
2024-06-28 | 92910 | 92.91 | 7.15 | 7.33 | 135 | 19 | 308 | 40 | 272 | 28 | NA | 600 | 0.3 | 23.31 | 1700000
2024-06-29 | 98220 | 98.22 | 7.14 | 7.35 | 130 | 20 | 296 | 44 | 265 | 32 | NA | 500 | 0.3 | 23.22 | 1300000
2024-06-30 | 96210 | 96.21 | 7.13 | 7.29 | 140 | 22 | 304 | 40 | 265 | 31 | NA | 400 | 0.3 | 23.1 | 1200000
Average | 100322.3333 | 100.3223 | 7.193 | 7.3813 | 133.1667 | 20.7 | 304.2667 | 43.3333 | 271.8667 | 34.2667 |  | 553.3333 | 0.3 | 23.1217 | 1353333.3333
3009.67
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 89860 | 89.86 | 7.11 | 7.24 | 125 | 18 | 292 | 40 | 260 | 28 |  | 400 | 0.3 | 22.18 | 1100000
Max | 108610 | 108.61 | 7.28 | 7.66 | 140 | 24 | 316 | 48 | 282 | 38 |  | 700 | 0.3 | 23.74 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-06-01 | 73320 | 73.32 | 7.04 | 7.97 | 145 | 18 | 280 | 44 | 269 | 27 | NA | 600 | 0.3 | 24.46 | 1400000
2024-06-02 | 72340 | 72.34 | 6.97 | 7.94 | 135 | 17 | 292 | 40 | 272 | 25 | NA | 500 | 0.3 | 23.33 | 1200000
2024-06-03 | 70620 | 70.62 | 6.89 | 7.95 | 130 | 18 | 300 | 44 | 263 | 26 | NA | 400 | 0.3 | 24.55 | 1300000
2024-06-04 | 72420 | 72.42 | 6.97 | 7.85 | 125 | 16 | 284 | 40 | 271 | 27 | NA | 600 | 0.3 | 23.25 | 1700000
2024-06-05 | 73520 | 73.52 | 6.98 | 7.97 | 130 | 17 | 276 | 40 | 268 | 26 | NA | 700 | 0.3 | 22.79 | 1400000
2024-06-06 | 73620 | 73.62 | 6.99 | 7.95 | 135 | 18 | 296 | 48 | 267 | 28 | NA | 500 | 0.3 | 22.72 | 1300000
2024-06-07 | 74540 | 74.54 | 6.97 | 7.93 | 140 | 16 | 292 | 44 | 271 | 25 | NA | 600 | 0.3 | 23.51 | 1400000
2024-06-08 | 71230 | 71.23 | 6.98 | 7.92 | 135 | 18 | 284 | 40 | 259 | 27 | NA | 700 | 0.3 | 22.9 | 1700000
2024-06-09 | 72740 | 72.74 | 7.02 | 7.95 | 130 | 17 | 288 | 44 | 265 | 26 | NA | 400 | 0.3 | 23.74 | 1200000
2024-06-10 | 70010 | 70.01 | 7.01 | 7.98 | 135 | 18 | 276 | 40 | 266 | 28 | NA | 600 | 0.3 | 24.46 | 1300000
2024-06-11 | 70880 | 70.88 | 6.97 | 7.92 | 130 | 17 | 292 | 44 | 273 | 25 | NA | 600 | 0.3 | 23.4 | 1400000
2024-06-12 | 67330 | 67.33 | 7.02 | 7.94 | 145 | 18 | 296 | 40 | 296 | 27 | NA | 600 | 0.3 | 23.56 | 1400000
2024-06-13 | 71480 | 71.48 | 6.98 | 7.93 | 140 | 18 | 268 | 44 | 280 | 26 | NA | 500 | 0.3 | 23.32 | 1400000
2024-06-14 | 70860 | 70.86 | 7.02 | 7.95 | 135 | 17 | 276 | 48 | 265 | 26 | NA | 600 | 0.3 | 23.32 | 1700000
2024-06-15 | 66220 | 66.22 | 7.05 | 7.95 | 130 | 18 | 292 | 44 | 275 | 27 | NA | 400 | 0.3 | 23.13 | 1300000
2024-06-16 | 70110 | 70.11 | 7.08 | 7.99 | 125 | 17 | 284 | 40 | 265 | 26 | NA | 500 | 0.3 | 24.64 | 1400000
2024-06-17 | 69900 | 69.9 | 7.06 | 7.84 | 130 | 17 | 220 | 40 | 112 | 13 | NA | 600 | 0.3 | 23.76 | 1200000
2024-06-18 | 69350 | 69.35 | 7.05 | 7.68 | 145 | 19 | 276 | 44 | 259 | 25 | NA | 400 | 0.3 | 22.87 | 1700000
2024-06-19 | 69900 | 69.9 | 7.07 | 7.71 | 130 | 18 | 272 | 44 | 253 | 26 | NA | 500 | 0.3 | 23.72 | 1300000
2024-06-20 | 71100 | 71.1 | 7.03 | 7.66 | 135 | 17 | 296 | 40 | 251 | 25 | NA | 600 | 0.3 | 24.24 | 1400000
2024-06-21 | 71360 | 71.36 | 7.09 | 7.65 | 130 | 18 | 292 | 44 | 265 | 28 | NA | 700 | 0.3 | 23.62 | 1700000
2024-06-22 | 75160 | 75.16 | 7.07 | 7.62 | 125 | 16 | 276 | 40 | 259 | 27 | NA | 500 | 0.3 | 23.63 | 1300000
2024-06-23 | 72220 | 72.22 | 7.23 | 7.64 | 130 | 17 | 284 | 44 | 255 | 26 | NA | 600 | 0.3 | 24.76 | 1200000
2024-06-24 | 74220 | 74.22 | 7.18 | 7.57 | 135 | 18 | 288 | 40 | 262 | 25 | NA | 400 | 0.3 | 23.85 | 1400000
2024-06-25 | 74720 | 74.72 | 7.36 | 7.67 | 125 | 17 | 296 | 44 | 263 | 26 | NA | 800 | 0.3 | 24.46 | 1100000
2024-06-26 | 75480 | 75.48 | 7.08 | 7.69 | 130 | 16 | 284 | 40 | 258 | 25 | NA | 400 | 0.3 | 24.68 | 1200000
2024-06-27 | 73980 | 73.98 | 7.02 | 7.64 | 140 | 18 | 272 | 40 | 265 | 24 | NA | 600 | 0.3 | 23.26 | 1400000
2024-06-28 | 76060 | 76.06 | 6.98 | 7.73 | 135 | 17 | 292 | 44 | 271 | 28 | NA | 700 | 0.3 | 22.75 | 1300000
2024-06-29 | 73680 | 73.68 | 7.09 | 7.74 | 125 | 16 | 276 | 40 | 264 | 26 | NA | 500 | 0.3 | 24.64 | 1700000
2024-06-30 | 73530 | 73.53 | 7.06 | 7.65 | 130 | 18 | 288 | 44 | 257 | 27 | NA | 400 | 0.3 | 23.58 | 1400000
Average | 72063.3333 | 72.0633 | 7.0437 | 7.8193 | 133 | 17.3333 | 282.9333 | 42.4 | 260.6333 | 25.7667 |  | 550 | 0.3 | 23.6967 | 1393333.3333
2161.9
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 66220 | 66.22 | 6.89 | 7.57 | 125 | 16 | 220 | 40 | 112 | 13 |  | 400 | 0.3 | 22.72 | 1100000
Max | 76060 | 76.06 | 7.36 | 7.99 | 145 | 19 | 300 | 48 | 296 | 28 |  | 800 | 0.3 | 24.76 | 1700000