## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-03-01 | 115720 | 115.72 | 7.23 | 7.34 | 140 | 24 | 292 | 48 | 276 | 42 | NA | 500 | 0.2 | 23.72 | 1700000
2024-03-02 | 104850 | 104.85 | 7.23 | 7.37 | 140 | 23 | 312 | 44 | 268 | 41 | NA | 700 | 0.3 | 22.47 | 1400000
2024-03-03 | 105030 | 105.03 | 7.17 | 7.35 | 135 | 22 | 316 | 40 | 275 | 38 | NA | 400 | 0.2 | 22.77 | 1700000
2024-03-04 | 117850 | 117.85 | 7.21 | 7.37 | 140 | 24 | 308 | 48 | 266 | 38 | NA | 600 | 0.3 | 22.6 | 1300000
2024-03-05 | 106970 | 106.97 | 7.23 | 7.35 | 130 | 21 | 296 | 40 | 273 | 36 | NA | 400 | 0.2 | 22.65 | 1400000
2024-03-06 | 102420 | 102.42 | 7.17 | 7.33 | 140 | 22 | 304 | 44 | 260 | 33 | NA | 500 | 0.3 | 23.82 | 1700000
2024-03-07 | 100400 | 100.4 | 7.22 | 7.37 | 135 | 23 | 308 | 42 | 265 | 37 | NA | 700 | 0.2 | 23.54 | 1300000
2024-03-08 | 109730 | 109.73 | 7.28 | 7.35 | 130 | 21 | 298 | 44 | 284 | 38 | NA | 500 | 0.3 | 24.36 | 1200000
2024-03-09 | 109940 | 109.94 | 7.24 | 7.31 | 125 | 24 | 312 | 46 | 260 | 36 | NA | 700 | 0.3 | 20.94 | 1700000
2024-03-10 | 113850 | 113.85 | 7.14 | 7.32 | 125 | 20 | 296 | 42 | 272 | 37 | NA | 800 | 0.2 | 22.06 | 1100000
2024-03-11 | 114370 | 114.37 | 7.2 | 7.36 | 135 | 21 | 312 | 44 | 263 | 35 | NA | 400 | 0.3 | 21.43 | 1400000
2024-03-12 | 121680 | 121.68 | 7.24 | 7.37 | 130 | 19 | 312 | 40 | 271 | 36 | NA | 500 | 0.2 | 22.6 | 1100000
2024-03-13 | 113900 | 113.9 | 7.17 | 7.35 | 135 | 23 | 300 | 44 | 282 | 33 | NA | 700 | 0.2 | 23.5 | 1200000
2024-03-14 | 113390 | 113.39 | 7.15 | 7.38 | 140 | 22 | 308 | 40 | 268 | 35 | NA | 700 | 0.3 | 23.7 | 1300000
2024-03-15 | 111510 | 111.51 | 7.09 | 7.33 | 135 | 21 | 312 | 44 | 273 | 37 | NA | 400 | 0.2 | 23.02 | 1700000
2024-03-16 | 112240 | 112.24 | 7.05 | 7.38 | 130 | 22 | 316 | 48 | 276 | 33 | NA | 500 | 0.3 | 22.65 | 1400000
2024-03-17 | 114160 | 114.16 | 7.03 | 7.41 | 135 | 21 | 304 | 44 | 266 | 37 | NA | 400 | 0.2 | 22.72 | 1200000
2024-03-18 | 110900 | 110.9 | 7.17 | 7.35 | 130 | 19 | 300 | 40 | 277 | 34 | NA | 700 | 0.3 | 22.44 | 1400000
2024-03-19 | 106910 | 106.91 | 7.2 | 7.4 | 125 | 20 | 304 | 44 | 268 | 34 | NA | 500 | 0.2 | 22.24 | 1700000
2024-03-20 | 105920 | 105.92 | 7.15 | 7.38 | 130 | 22 | 300 | 40 | 266 | 33 | NA | 400 | 0.3 | 22.28 | 1400000
2024-03-21 | 100890 | 100.89 | 7.21 | 7.42 | 140 | 20 | 308 | 40 | 260 | 34 | NA | 700 | 0.3 | 22.87 | 1300000
2024-03-22 | 106180 | 106.18 | 7.2 | 7.45 | 130 | 22 | 296 | 44 | 255 | 35 | NA | 600 | 0.2 | 22.97 | 1700000
2024-03-23 | 104680 | 104.68 | 7.23 | 7.43 | 125 | 24 | 292 | 44 | 250 | 33 | NA | 400 | 0.2 | 22.92 | 1400000
2024-03-24 | 115700 | 115.7 | 7.19 | 7.4 | 140 | 20 | 280 | 40 | 253 | 34 | NA | 500 | 0.3 | 23.04 | 1200000
2024-03-25 | 127290 | 127.29 | 7.22 | 7.43 | 135 | 23 | 288 | 40 | 265 | 34 | NA | 700 | 0.2 | 22.36 | 1400000
2024-03-26 | 118640 | 118.64 | 7.25 | 7.36 | 130 | 25 | 292 | 48 | 266 | 32 | NA | 500 | 0.3 | 23.07 | 1200000
2024-03-27 | 107040 | 107.04 | 7.23 | 7.41 | 120 | 22 | 304 | 44 | 272 | 33 | NA | 600 | 0.2 | 23.32 | 1700000
2024-03-28 | 106150 | 106.15 | 7.26 | 7.43 | 135 | 20 | 300 | 40 | 268 | 36 | NA | 500 | 0.3 | 23.62 | 1400000
2024-03-29 | 105890 | 105.89 | 7.19 | 7.45 | 140 | 22 | 292 | 44 | 282 | 37 | NA | 400 | 0.2 | 22.86 | 1700000
2024-03-30 | 104000 | 104 | 7.25 | 7.47 | 130 | 21 | 308 | 40 | 276 | 35 | NA | 700 | 0.3 | 22.54 | 1300000
2024-03-31 | 103470 | 103.47 | 7.31 | 7.44 | 135 | 24 | 300 | 48 | 268 | 33 | NA | 500 | 0.3 | 23.06 | 1400000
Average | 110053.871 | 110.0539 | 7.1971 | 7.3826 | 133.0645 | 21.8387 | 302.2581 | 43.1613 | 268.5161 | 35.4516 |  | 551.6129 | 0.25161 | 22.8432 | 1419354.8387
3411.67
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 100400 | 100.4 | 7.03 | 7.31 | 120 | 19 | 280 | 40 | 250 | 32 |  | 400 | 0.2 | 20.94 | 1100000
Max | 127290 | 127.29 | 7.31 | 7.47 | 140 | 25 | 316 | 48 | 284 | 42 |  | 800 | 0.3 | 24.36 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-03-01 | 80280 | 80.28 | 7.05 | 7.75 | 130 | 17 | 276 | 44 | 258 | 26 | NA | 600 | 0.3 | 24 | 1400000
2024-03-02 | 75270 | 75.27 | 7.07 | 7.76 | 135 | 18 | 292 | 48 | 268 | 27 | NA | 500 | 0.3 | 23.73 | 1700000
2024-03-03 | 90190 | 90.19 | 6.98 | 7.71 | 130 | 16 | 288 | 44 | 263 | 28 | NA | 400 | 0.3 | 24.31 | 1200000
2024-03-04 | 77790 | 77.79 | 7.02 | 7.67 | 135 | 18 | 284 | 44 | 256 | 25 | NA | 700 | 0.2 | 23.73 | 1400000
2024-03-05 | 75820 | 75.82 | 7.06 | 7.75 | 125 | 17 | 280 | 48 | 268 | 26 | NA | 600 | 0.3 | 22.7 | 1700000
2024-03-06 | 73120 | 73.12 | 7.12 | 7.81 | 140 | 18 | 288 | 44 | 270 | 25 | NA | 500 | 0.3 | 22.4 | 1300000
2024-03-07 | 74180 | 74.18 | 7.09 | 7.78 | 130 | 16 | 292 | 48 | 261 | 27 | NA | 400 | 0.3 | 23.33 | 1400000
2024-03-08 | 77900 | 77.9 | 7.13 | 7.82 | 135 | 17 | 296 | 48 | 265 | 26 | NA | 600 | 0.2 | 23.31 | 1300000
2024-03-09 | 73620 | 73.62 | 7.1 | 7.77 | 125 | 16 | 284 | 40 | 269 | 28 | NA | 700 | 0.3 | 22.53 | 1700000
2024-03-10 | 76370 | 76.37 | 7.06 | 7.74 | 135 | 18 | 288 | 44 | 271 | 27 | NA | 600 | 0.3 | 23.58 | 1300000
2024-03-11 | 74930 | 74.93 | 7.02 | 7.76 | 130 | 17 | 300 | 44 | 265 | 26 | NA | 500 | 0.3 | 23.2 | 1400000
2024-03-12 | 77960 | 77.96 | 7.05 | 7.74 | 135 | 16 | 276 | 40 | 268 | 26 | NA | 400 | 0.3 | 22.39 | 1200000
2024-03-13 | 77120 | 77.12 | 7.02 | 7.65 | 125 | 17 | 260 | 40 | 265 | 28 | NA | 600 | 0.2 | 23.57 | 1700000
2024-03-14 | 76570 | 76.57 | 6.89 | 7.55 | 130 | 16 | 284 | 44 | 257 | 26 | NA | 500 | 0.3 | 23.95 | 1300000
2024-03-15 | 77400 | 77.4 | 6.93 | 7.58 | 125 | 16 | 288 | 40 | 262 | 28 | NA | 700 | 0.3 | 24.23 | 1400000
2024-03-16 | 77660 | 77.66 | 6.95 | 7.64 | 130 | 17 | 296 | 48 | 273 | 27 | NA | 600 | 0.2 | 22.83 | 1200000
2024-03-17 | 77820 | 77.82 | 7.05 | 7.61 | 135 | 18 | 292 | 44 | 259 | 28 | NA | 400 | 0.3 | 23.83 | 1700000
2024-03-18 | 76100 | 76.1 | 7.04 | 7.67 | 125 | 16 | 280 | 40 | 271 | 27 | NA | 500 | 0.3 | 23.4 | 1400000
2024-03-19 | 72930 | 72.93 | 7.03 | 7.72 | 135 | 18 | 288 | 44 | 263 | 28 | NA | 600 | 0.3 | 22.87 | 1200000
2024-03-20 | 76970 | 76.97 | 7.06 | 7.63 | 130 | 17 | 296 | 48 | 274 | 27 | NA | 700 | 0.3 | 23.75 | 1700000
2024-03-21 | 76510 | 76.51 | 7.07 | 7.69 | 135 | 18 | 292 | 44 | 261 | 26 | NA | 600 | 0.2 | 22.85 | 1400000
2024-03-22 | 73800 | 73.8 | 7.14 | 7.73 | 130 | 17 | 304 | 44 | 274 | 25 | NA | 500 | 0.3 | 23.51 | 1300000
2024-03-23 | 75310 | 75.31 | 7.06 | 7.68 | 125 | 16 | 284 | 40 | 263 | 26 | NA | 400 | 0.3 | 24.21 | 1200000
2024-03-24 | 76460 | 76.46 | 7.05 | 7.66 | 130 | 17 | 280 | 44 | 259 | 25 | NA | 700 | 0.2 | 23.66 | 1700000
2024-03-25 | 80400 | 80.4 | 7.03 | 7.47 | 135 | 18 | 276 | 48 | 257 | 26 | NA | 500 | 0.3 | 22.86 | 1400000
2024-03-26 | 82150 | 82.15 | 7.01 | 7.42 | 125 | 15 | 260 | 44 | 271 | 25 | NA | 600 | 0.3 | 23.51 | 1300000
2024-03-27 | 76720 | 76.72 | 7.09 | 7.31 | 130 | 16 | 284 | 44 | 264 | 26 | NA | 400 | 0.3 | 23.58 | 1400000
2024-03-28 | 72430 | 72.43 | 6.98 | 7.05 | 125 | 15 | 272 | 40 | 263 | 25 | NA | 700 | 0.2 | 22.66 | 1700000
2024-03-29 | 68520 | 68.52 | 7.02 | 7.08 | 130 | 17 | 288 | 44 | 265 | 27 | NA | 600 | 0.3 | 24.02 | 1400000
2024-03-30 | 75500 | 75.5 | 7.14 | 7.49 | 135 | 18 | 292 | 40 | 273 | 26 | NA | 500 | 0.3 | 23.79 | 1300000
2024-03-31 | 73610 | 73.61 | 7.1 | 7.46 | 130 | 16 | 304 | 48 | 276 | 28 | NA | 600 | 0.3 | 24.19 | 1700000
Average | 76497.0968 | 76.4971 | 7.0455 | 7.6177 | 130.6452 | 16.8387 | 285.9355 | 44 | 265.5484 | 26.4839 |  | 554.8387 | 0.27742 | 23.4348 | 1432258.0645
2371.41
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 68520 | 68.52 | 6.89 | 7.05 | 125 | 15 | 260 | 40 | 256 | 25 |  | 400 | 0.2 | 22.39 | 1200000
Max | 90190 | 90.19 | 7.14 | 7.82 | 140 | 18 | 304 | 48 | 276 | 28 |  | 700 | 0.3 | 24.31 | 1700000