## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-05-01 | 97730 | 97.73 | 7.35 | 7.38 | 135 | 20 | 312 | 44 | 271 | 35 | NA | 500 | 0.3 | 23.06 | 1200000
2024-05-02 | 98770 | 98.77 | 7.23 | 7.35 | 140 | 21 | 316 | 40 | 278 | 36 | NA | 700 | 0.3 | 23.2 | 1700000
2024-05-03 | 101120 | 101.12 | 7.21 | 7.37 | 135 | 22 | 308 | 44 | 268 | 34 | NA | 400 | 0.3 | 23.73 | 1100000
2024-05-04 | 104930 | 104.93 | 7.22 | 7.38 | 140 | 20 | 300 | 40 | 273 | 35 | NA | 600 | 0.3 | 23.6 | 1300000
2024-05-05 | 102440 | 102.44 | 7.19 | 7.35 | 135 | 19 | 312 | 44 | 279 | 36 | NA | 500 | 0.3 | 23.07 | 1400000
2024-05-06 | 104130 | 104.13 | 7.23 | 7.38 | 140 | 22 | 304 | 40 | 271 | 33 | NA | 700 | 0.3 | 23.8 | 1200000
2024-05-07 | 105390 | 105.39 | 7.21 | 7.32 | 135 | 19 | 304 | 44 | 268 | 35 | NA | 700 | 0.3 | 23.01 | 1700000
2024-05-08 | 101230 | 101.23 | 7.25 | 7.33 | 130 | 20 | 300 | 44 | 275 | 34 | NA | 500 | 0.3 | 22.89 | 1200000
2024-05-09 | 106460 | 106.46 | 7.22 | 7.35 | 140 | 19 | 296 | 40 | 270 | 36 | NA | 700 | 0.3 | 23.36 | 1300000
2024-05-10 | 102040 | 102.04 | 7.27 | 7.37 | 135 | 18 | 300 | 40 | 267 | 34 | NA | 700 | 0.3 | 23.4 | 1100000
2024-05-11 | 100300 | 100.3 | 7.25 | 7.39 | 125 | 19 | 296 | 44 | 277 | 35 | NA | 600 | 0.3 | 23.68 | 1200000
2024-05-12 | 96580 | 96.58 | 7.19 | 7.41 | 130 | 22 | 304 | 40 | 268 | 33 | NA | 400 | 0.3 | 23.44 | 1700000
2024-05-13 | 99220 | 99.22 | 7.21 | 7.44 | 135 | 20 | 308 | 44 | 276 | 34 | NA | 600 | 0.3 | 23.07 | 1400000
2024-05-14 | 99660 | 99.66 | 7.23 | 7.37 | 140 | 18 | 312 | 40 | 270 | 35 | NA | 500 | 0.3 | 23.17 | 1300000
2024-05-15 | 96350 | 96.35 | 7.21 | 7.39 | 130 | 21 | 304 | 40 | 273 | 36 | NA | 700 | 0.3 | 23.1 | 1100000
2024-05-16 | 95280 | 95.28 | 7.24 | 7.35 | 125 | 19 | 312 | 44 | 282 | 34 | NA | 600 | 0.3 | 23.11 | 1700000
2024-05-17 | 101590 | 101.59 | 7.26 | 7.39 | 130 | 18 | 308 | 44 | 275 | 36 | NA | 500 | 0.3 | 23.54 | 1200000
2024-05-18 | 101230 | 101.23 | 7.28 | 7.47 | 135 | 20 | 300 | 40 | 269 | 35 | NA | 400 | 0.3 | 23.56 | 1400000
2024-05-19 | 95600 | 95.6 | 7.23 | 7.45 | 140 | 21 | 308 | 44 | 280 | 37 | NA | 700 | 0.3 | 22.96 | 1300000
2024-05-20 | 96060 | 96.06 | 7.19 | 7.53 | 130 | 23 | 312 | 48 | 278 | 36 | NA | 600 | 0.3 | 23.9 | 1100000
2024-05-21 | 93360 | 93.36 | 7.25 | 7.49 | 135 | 22 | 316 | 48 | 277 | 33 | NA | 500 | 0.3 | 23.16 | 1200000
2024-05-22 | 94200 | 94.2 | 7.23 | 7.47 | 130 | 19 | 304 | 44 | 284 | 32 | NA | 800 | 0.3 | 23.22 | 1700000
2024-05-23 | 92870 | 92.87 | 7.24 | 7.49 | 125 | 21 | 300 | 40 | 262 | 34 | NA | 400 | 0.3 | 23.02 | 1300000
2024-05-24 | 104490 | 104.49 | 7.23 | 7.48 | 130 | 20 | 296 | 44 | 275 | 36 | NA | 600 | 0.3 | 23.25 | 1400000
2024-05-25 | 99910 | 99.91 | 7.19 | 7.56 | 125 | 22 | 304 | 48 | 270 | 37 | NA | 700 | 0.3 | 23.09 | 1100000
2024-05-26 | 98060 | 98.06 | 7.23 | 7.55 | 130 | 21 | 300 | 44 | 268 | 35 | NA | 500 | 0.3 | 23.1 | 1200000
2024-05-27 | 97950 | 97.95 | 7.17 | 7.52 | 125 | 20 | 292 | 48 | 260 | 37 | NA | 400 | 0.3 | 23.54 | 1300000
2024-05-28 | 96820 | 96.82 | 7.22 | 7.54 | 135 | 19 | 308 | 44 | 265 | 38 | NA | 600 | 0.3 | 23.17 | 1400000
2024-05-29 | 93530 | 93.53 | 7.25 | 7.49 | 140 | 22 | 296 | 44 | 257 | 36 | NA | 700 | 0.3 | 23.14 | 1700000
2024-05-30 | 95040 | 95.04 | 7.18 | 7.5 | 135 | 21 | 300 | 40 | 265 | 35 | NA | 500 | 0.3 | 24.1 | 1200000
2024-05-31 | 95700 | 95.7 | 7.27 | 7.47 | 140 | 20 | 312 | 44 | 271 | 34 | NA | 700 | 0.3 | 23.75 | 1400000
Average | 98969.0323 | 98.969 | 7.23 | 7.43 | 133.3871 | 20.2581 | 304.6452 | 43.0968 | 271.6774 | 35.0323 |  | 580.6452 | 0.3 | 23.3287 | 1338709.6774
3068.04
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 92870 | 92.87 | 7.17 | 7.32 | 125 | 18 | 292 | 40 | 257 | 32 |  | 400 | 0.3 | 22.89 | 1100000
Max | 106460 | 106.46 | 7.35 | 7.56 | 140 | 23 | 316 | 48 | 284 | 38 |  | 800 | 0.3 | 24.1 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-05-01 | 73650 | 73.65 | 7.12 | 7.92 | 135 | 16 | 292 | 40 | 274 | 27 | NA | 400 | 0.3 | 23.81 | 1300000
2024-05-02 | 71920 | 71.92 | 7.11 | 7.91 | 140 | 17 | 304 | 44 | 269 | 24 | NA | 700 | 0.3 | 22.19 | 1700000
2024-05-03 | 72100 | 72.1 | 7.1 | 7.97 | 125 | 16 | 280 | 40 | 262 | 26 | NA | 600 | 0.3 | 22.39 | 1400000
2024-05-04 | 76140 | 76.14 | 7.07 | 7.95 | 135 | 17 | 288 | 44 | 274 | 24 | NA | 500 | 0.3 | 22.45 | 1200000
2024-05-05 | 76250 | 76.25 | 7.04 | 8.01 | 140 | 18 | 300 | 40 | 279 | 26 | NA | 400 | 0.3 | 23.23 | 1300000
2024-05-06 | 74910 | 74.91 | 7.03 | 7.9 | 140 | 17 | 276 | 44 | 264 | 25 | NA | 600 | 0.3 | 23.36 | 1700000
2024-05-07 | 74660 | 74.66 | 7.02 | 7.91 | 135 | 18 | 284 | 48 | 261 | 27 | NA | 500 | 0.3 | 22.6 | 1400000
2024-05-08 | 75730 | 75.73 | 7.05 | 7.96 | 130 | 17 | 288 | 44 | 266 | 26 | NA | 700 | 0.3 | 22.6 | 1700000
2024-05-09 | 74400 | 74.4 | 7.07 | 7.98 | 140 | 18 | 296 | 40 | 272 | 25 | NA | 400 | 0.3 | 22.72 | 1200000
2024-05-10 | 75420 | 75.42 | 7.09 | 7.83 | 135 | 18 | 292 | 44 | 259 | 24 | NA | 600 | 0.3 | 21.63 | 1400000
2024-05-11 | 72150 | 72.15 | 7.1 | 7.85 | 130 | 17 | 280 | 40 | 265 | 27 | NA | 400 | 0.3 | 22.31 | 1300000
2024-05-12 | 72400 | 72.4 | 7.08 | 7.82 | 140 | 18 | 284 | 48 | 261 | 28 | NA | 700 | 0.3 | 22.33 | 1700000
2024-05-13 | 72620 | 72.62 | 7.11 | 7.86 | 135 | 16 | 292 | 44 | 272 | 26 | NA | 400 | 0.3 | 23.08 | 1200000
2024-05-14 | 73710 | 73.71 | 7.17 | 7.85 | 145 | 19 | 276 | 48 | 280 | 28 | NA | 500 | 0.3 | 24.12 | 1400000
2024-05-15 | 71970 | 71.97 | 7.22 | 7.81 | 140 | 18 | 280 | 44 | 275 | 26 | NA | 600 | 0.3 | 24.09 | 1700000
2024-05-16 | 71950 | 71.95 | 7.18 | 7.85 | 135 | 17 | 276 | 48 | 266 | 25 | NA | 400 | 0.3 | 22.83 | 1300000
2024-05-17 | 72520 | 72.52 | 7.13 | 7.95 | 125 | 16 | 284 | 40 | 258 | 27 | NA | 600 | 0.3 | 23.32 | 1400000
2024-05-18 | 72030 | 72.03 | 7.14 | 7.91 | 130 | 17 | 292 | 44 | 267 | 26 | NA | 500 | 0.3 | 23.23 | 1200000
2024-05-19 | 75820 | 75.82 | 7.1 | 7.8 | 135 | 18 | 296 | 44 | 271 | 28 | NA | 400 | 0.3 | 22.65 | 1700000
2024-05-20 | 75420 | 75.42 | 7.12 | 7.78 | 130 | 17 | 284 | 40 | 264 | 27 | NA | 700 | 0.3 | 23.07 | 1400000
2024-05-21 | 74590 | 74.59 | 7.05 | 7.84 | 125 | 16 | 276 | 40 | 267 | 26 | NA | 500 | 0.3 | 22.87 | 1300000
2024-05-22 | 74520 | 74.52 | 7.07 | 7.83 | 140 | 18 | 288 | 44 | 274 | 27 | NA | 600 | 0.3 | 23.73 | 1400000
2024-05-23 | 76350 | 76.35 | 7.03 | 7.79 | 145 | 19 | 296 | 48 | 269 | 25 | NA | 700 | 0.3 | 22.5 | 1400000
2024-05-24 | 77400 | 77.4 | 7.02 | 7.63 | 140 | 18 | 268 | 40 | 263 | 26 | NA | 400 | 0.3 | 23.79 | 1700000
2024-05-25 | 73520 | 73.52 | 7.01 | 7.82 | 135 | 17 | 292 | 48 | 271 | 28 | NA | 600 | 0.3 | 22.97 | 1400000
2024-05-26 | 77620 | 77.62 | 7.03 | 7.87 | 145 | 18 | 272 | 44 | 262 | 26 | NA | 400 | 0.3 | 22.7 | 1300000
2024-05-27 | 75870 | 75.87 | 7.02 | 7.85 | 130 | 16 | 276 | 40 | 264 | 27 | NA | 500 | 0.3 | 23.65 | 1700000
2024-05-28 | 74840 | 74.84 | 7.05 | 7.89 | 135 | 17 | 284 | 44 | 259 | 25 | NA | 600 | 0.3 | 22.57 | 1200000
2024-05-29 | 73480 | 73.48 | 7.09 | 7.9 | 140 | 18 | 288 | 40 | 273 | 27 | NA | 400 | 0.3 | 24.12 | 1400000
2024-05-30 | 72860 | 72.86 | 7.07 | 7.95 | 130 | 16 | 284 | 44 | 267 | 26 | NA | 500 | 0.3 | 23.69 | 1300000
2024-05-31 | 74820 | 74.82 | 7.02 | 7.93 | 140 | 18 | 276 | 40 | 261 | 25 | NA | 700 | 0.3 | 22.85 | 1700000
Average | 74246.4516 | 74.2465 | 7.081 | 7.8748 | 135.6452 | 17.2903 | 285.2903 | 43.2258 | 267.3871 | 26.129 |  | 532.2581 | 0.3 | 23.0145 | 1432258.0645
2301.64
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 71920 | 71.92 | 7.01 | 7.63 | 125 | 16 | 268 | 40 | 258 | 24 |  | 400 | 0.3 | 21.63 | 1200000
Max | 77620 | 77.62 | 7.22 | 8.01 | 145 | 19 | 304 | 48 | 280 | 28 |  | 700 | 0.3 | 24.12 | 1700000