## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-11-01 | 117030 | 117.03 | 7.28 | 7.36 | 129 | 23 | 336 | 48 | 303 | 29 | NA | 600 | 0.2 | 25.4 | 1400000
2022-11-02 | 112470 | 112.47 | 7.31 | 7.38 | 135 | 22 | 332 | 40 | 308 | 28 | NA | 700 | 0.3 | 25.1 | 1300000
2022-11-03 | 114810 | 114.81 | 7.29 | 7.33 | 140 | 24 | 340 | 47 | 303 | 31 | NA | 800 | 0.2 | 24.8 | 1700000
2022-11-04 | 123930 | 123.93 | 7.33 | 7.36 | 130 | 25 | 332 | 45 | 298 | 27 | NA | 400 | 0.3 | 25 | 1400000
2022-11-05 | 115780 | 115.78 | 7.28 | 7.39 | 135 | 24 | 334 | 44 | 305 | 30 | NA | 500 | 0.2 | 24.8 | 1200000
2022-11-06 | 115510 | 115.51 | 7.33 | 7.36 | 140 | 24 | 338 | 48 | 294 | 28 | NA | 600 | 0.3 | 25.4 | 1700000
2022-11-07 | 113140 | 113.14 | 7.27 | 7.33 | 145 | 23 | 327 | 46 | 292 | 32 | NA | 800 | 0.2 | 25.2 | 1300000
2022-11-08 | 113860 | 113.86 | 7.29 | 7.38 | 135 | 22 | 339 | 42 | 298 | 33 | NA | 400 | 0.3 | 24.6 | 1100000
2022-11-09 | 114810 | 114.81 | 7.31 | 7.33 | 130 | 22 | 324 | 44 | 295 | 31 | NA | 700 | 0.2 | 25.2 | 1400000
2022-11-10 | 115840 | 115.84 | 7.29 | 7.34 | 135 | 24 | 334 | 47 | 288 | 35 | NA | 600 | 0.3 | 24.6 | 1700000
2022-11-11 | 114800 | 114.8 | 7.26 | 7.33 | 125 | 26 | 330 | 40 | 291 | 31 | NA | 700 | 0.2 | 24.9 | 1400000
2022-11-12 | 112200 | 112.2 | 7.29 | 7.38 | 145 | 22 | 335 | 44 | 303 | 32 | NA | 600 | 0.3 | 24.8 | 1700000
2022-11-13 | 117800 | 117.8 | 7.33 | 7.37 | 130 | 21 | 364 | 47 | 307 | 36 | NA | 600 | 0.2 | 25.3 | 1700000
2022-11-14 | 117280 | 117.28 | 7.33 | 7.38 | 125 | 23 | 332 | 45 | 295 | 34 | NA | 700 | 0.3 | 24.01 | 1400000
2022-11-15 | 109590 | 109.59 | 7.31 | 7.36 | 140 | 24 | 330 | 44 | 303 | 31 | NA | 500 | 0.2 | 25.1 | 1300000
2022-11-16 | 112120 | 112.12 | 7.34 | 7.41 | 135 | 21 | 336 | 42 | 298 | 36 | NA | 400 | 0.3 | 25.19 | 1200000
2022-11-17 | 112140 | 112.14 | 7.29 | 7.44 | 130 | 25 | 322 | 49 | 286 | 31 | NA | 600 | 0.2 | 24.6 | 1700000
2022-11-18 | 112300 | 112.3 | 7.35 | 7.38 | 130 | 21 | 325 | 42 | 288 | 30 | NA | 500 | 0.3 | 24.8 | 1200000
2022-11-19 | 111750 | 111.75 | 7.28 | 7.36 | 145 | 23 | 340 | 47 | 303 | 33 | NA | 400 | 0.5 | 25.2 | 1400000
2022-11-20 | 116130 | 116.13 | 7.31 | 7.37 | 130 | 25 | 336 | 48 | 294 | 35 | NA | 700 | 0.5 | 24.7 | 1300000
2022-11-21 | 111110 | 111.11 | 7.29 | 7.39 | 125 | 24 | 328 | 45 | 301 | 30 | NA | 200 | 0.5 | 24.6 | 1700000
2022-11-22 | 113300 | 112.3 | 7.33 | 7.41 | 135 | 23 | 334 | 40 | 306 | 34 | NA | 200 | 0.5 | 24.6 | 1400000
2022-11-23 | 114140 | 114.14 | 7.31 | 7.35 | 130 | 26 | 340 | 47 | 292 | 28 | NA | 500 | 0.4 | 24.9 | 1200000
2022-11-24 | 107540 | 107.54 | 7.33 | 7.38 | 140 | 23 | 330 | 40 | 304 | 33 | NA | 700 | 0.5 | 24.6 | 1400000
2022-11-25 | 115190 | 115.19 | 7.28 | 7.41 | 135 | 20 | 336 | 44 | 298 | 35 | NA | 600 | 0.4 | 24.5 | 1700000
2022-11-26 | 109540 | 109.54 | 7.32 | 7.46 | 145 | 19 | 328 | 40 | 296 | 32 | NA | 700 | 0.3 | 25.18 | 1300000
2022-11-27 | 110290 | 110.29 | 7.26 | 7.38 | 140 | 23 | 340 | 42 | 309 | 34 | NA | 500 | 0.3 | 25.5 | 1200000
2022-11-28 | 112790 | 112.79 | 7.48 | 7.56 | 135 | 23 | 328 | 40 | 298 | 36 | NA | 400 | 0.2 | 24.68 | 1100000
2022-11-29 | 116790 | 116.79 | 7.28 | 7.41 | 140 | 22 | 338 | 47 | 305 | 33 | NA | 200 | 0.2 | 24.4 | 1400000
2022-11-30 | 121080 | 121.08 | 7.33 | 7.49 | 130 | 25 | 340 | 44 | 302 | 30 | NA | 500 | 0.3 | 24.9 | 1700000
Average | 114168.6667 | 114.1353 | 7.3093 | 7.386 | 134.8 | 23.0667 | 334.2667 | 44.2667 | 298.7667 | 31.9333 | NA | 543.3333 | 0.30333 | 24.8853 | 1420000
| 3425060 | 3424.06
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 107540 | 107.54 | 7.26 | 7.33 | 125 | 19 | 322 | 40 | 286 | 27 |  | 200 | 0.2 | 24.01 | 1100000
Max | 123930 | 123.93 | 7.48 | 7.56 | 145 | 26 | 364 | 49 | 309 | 36 |  | 800 | 0.5 | 25.5 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-11-01 | 70520 | 70.52 | 7.33 | 7.68 | 136 | 16 | 340 | 44 | 309 | 25 | NA | 700 | 0.2 | 22.17 | 1700000 | Retaining wall at tapping point of Rajapur SPS is broken, hence raw sewage is going directly into the river.
2022-11-02 | 71640 | 71.64 | 7.38 | 7.7 | 126 | 17 | 336 | 40 | 285 | 26 | NA | 500 | 0.3 | 22.4 | 1400000
2022-11-03 | 73930 | 73.93 | 7.45 | 7.72 | 145 | 18 | 324 | 44 | 312 | 26 | NA | 600 | 0.2 | 23.37 | 1700000
2022-11-04 | 75840 | 75.84 | 7.34 | 7.77 | 140 | 18 | 332 | 44 | 295 | 24 | NA | 500 | 0.2 | 24.28 | 1400000
2022-11-05 | 81960 | 81.96 | 7.41 | 7.75 | 145 | 17 | 328 | 40 | 298 | 26 | NA | 400 | 0.3 | 22.27 | 1300000
2022-11-06 | 78030 | 78.03 | 7.38 | 7.72 | 140 | 16 | 332 | 36 | 287 | 23 | NA | 500 | 0.2 | 23.36 | 1700000
2022-11-07 | 80150 | 80.15 | 7.28 | 7.65 | 135 | 17 | 316 | 40 | 297 | 24 | NA | 600 | 0.2 | 23.26 | 1400000
2022-11-08 | 75650 | 75.65 | 7.25 | 7.61 | 130 | 16 | 324 | 44 | 298 | 25 | NA | 700 | 0.2 | 23.32 | 1700000
2022-11-09 | 80530 | 80.53 | 7.41 | 7.77 | 125 | 18 | 312 | 44 | 269 | 26 | NA | 500 | 0.3 | 24 | 1400000
2022-11-10 | 73610 | 73.61 | 7.33 | 7.72 | 130 | 17 | 324 | 40 | 283 | 25 | NA | 400 | 0.3 | 22.86 | 1300000
2022-11-11 | 76540 | 76.54 | 7.43 | 7.61 | 150 | 19 | 328 | 44 | 272 | 27 | NA | 700 | 0.2 | 23.49 | 1400000
2022-11-12 | 78460 | 78.46 | 7.27 | 7.63 | 145 | 16 | 312 | 44 | 265 | 24 | NA | 500 | 0.2 | 23.08 | 1700000
2022-11-13 | 82760 | 82.76 | 7.38 | 7.69 | 135 | 17 | 304 | 40 | 275 | 26 | NA | 700 | 0.3 | 23.64 | 1700000
2022-11-14 | 77650 | 77.65 | 7.42 | 7.71 | 130 | 18 | 284 | 44 | 269 | 27 | NA | 400 | 0.2 | 23.24 | 1400000
2022-11-15 | 78670 | 78.67 | 7.33 | 7.68 | 125 | 16 | 292 | 40 | 265 | 25 | NA | 500 | 0.3 | 24.4 | 1700000
2022-11-16 | 76430 | 76.43 | 7.6 | 7.85 | 135 | 17 | 324 | 44 | 283 | 27 | NA | 600 | 0.2 | 23.32 | 1300000
2022-11-17 | 83790 | 83.79 | 7.52 | 7.78 | 140 | 16 | 316 | 36 | 268 | 25 | NA | 700 | 0.2 | 24.22 | 1400000
2022-11-18 | 83200 | 83.2 | 7.46 | 7.75 | 130 | 17 | 328 | 40 | 295 | 26 | NA | 500 | 0.3 | 23.26 | 1300000
2022-11-19 | 79310 | 79.31 | 7.57 | 7.79 | 145 | 18 | 320 | 44 | 287 | 24 | NA | 600 | 0.2 | 24.22 | 1700000
2022-11-20 | 80630 | 80.63 | 7.43 | 7.72 | 135 | 19 | 312 | 40 | 276 | 27 | NA | 400 | 0.2 | 23.21 | 1300000
2022-11-21 | 85510 | 85.51 | 7.45 | 7.81 | 150 | 18 | 336 | 44 | 263 | 26 | NA | 500 | 0.3 | 24.51 | 1400000
2022-11-22 | 84520 | 84.52 | 7.52 | 7.78 | 140 | 17 | 328 | 40 | 291 | 23 | NA | 700 | 0.2 | 23.67 | 1700000
2022-11-23 | 83620 | 83.62 | 7.52 | 7.79 | 130 | 16 | 324 | 36 | 285 | 24 | NA | 600 | 0.3 | 23.22 | 1400000
2022-11-24 | 86220 | 86.22 | 7.48 | 7.76 | 125 | 17 | 332 | 40 | 292 | 26 | NA | 500 | 0.2 | 24.15 | 1300000
2022-11-25 | 83720 | 83.72 | 7.45 | 7.69 | 140 | 18 | 312 | 44 | 281 | 25 | NA | 600 | 0.2 | 23.21 | 1700000
2022-11-26 | 81950 | 81.95 | 7.38 | 7.76 | 145 | 17 | 324 | 40 | 274 | 23 | NA | 700 | 0.3 | 22.86 | 1400000
2022-11-27 | 83780 | 83.78 | 7.41 | 7.73 | 135 | 19 | 308 | 44 | 283 | 24 | NA | 400 | 0.2 | 23.31 | 1300000
2022-11-28 | 78100 | 78.1 | 7.62 | 7.85 | 140 | 17 | 336 | 40 | 298 | 26 | NA | 600 | 0.2 | 23.54 | 1400000
2022-11-29 | 80890 | 80.89 | 7.54 | 7.83 | 130 | 18 | 324 | 44 | 276 | 27 | NA | 500 | 0.2 | 24.02 | 1700000
2022-11-30 | 79220 | 79.22 | 7.56 | 7.81 | 140 | 17 | 332 | 44 | 282 | 26 | NA | 700 | 0.3 | 24.49 | 1400000
Average | 79561 | 79.561 | 7.43 | 7.737 | 136.5667 | 17.2333 | 321.4667 | 41.6 | 283.7667 | 25.2667 | NA | 560 | 0.23667 | 23.4783 | 1486666.6667
| 2386830 | 2386.83
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 70520 | 70.52 | 7.25 | 7.61 | 125 | 16 | 284 | 36 | 263 | 23 |  | 400 | 0.2 | 22.17 | 1300000
Max | 86220 | 86.22 | 7.62 | 7.85 | 150 | 19 | 340 | 44 | 312 | 27 |  | 700 | 0.3 | 24.51 | 1700000