## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-10-01 | 118880 | 118.88 | 7.28 | 7.36 | 136 | 20 | 340 | 40 | 304 | 35 | NA | 500 | 0.3 | 25.3 | 1300000
2022-10-02 | 118560 | 118.56 | 7.33 | 7.37 | 123 | 23 | 316 | 48 | 288 | 30 | NA | 700 | 0.2 | 25.5 | 1700000
2022-10-03 | 114800 | 114.5 | 7.28 | 7.36 | 129 | 20 | 320 | 40 | 307 | 29 | NA | 600 | 0.3 | 25.7 | 1400000
2022-10-04 | 110760 | 110.76 | 7.32 | 7.35 | 123 | 22 | 312 | 44 | 298 | 31 | NA | 400 | 0.3 | 25.2 | 1200000
2022-10-05 | 166290 | 116.29 | 7.28 | 7.33 | 126 | 19 | 320 | 40 | 294 | 32 | NA | 500 | 0.4 | 25.3 | 1300000
2022-10-06 | 109560 | 109.56 | 7.31 | 7.34 | 139 | 20 | 328 | 48 | 292 | 29 | NA | 700 | 0.3 | 25.4 | 1700000
2022-10-07 | 123000 | 123 | 7.32 | 7.36 | 129 | 24 | 336 | 40 | 302 | 31 | NA | 800 | 0.2 | 25.2 | 1400000
2022-10-08 | 133470 | 133.47 | 7.33 | 7.36 | 133 | 22 | 340 | 44 | 306 | 30 | NA | 600 | 0.2 | 25.3 | 1200000
2022-10-09 | 126280 | 126.28 | 7.28 | 7.35 | 129 | 20 | 324 | 40 | 302 | 27 | NA | 800 | 0.3 | 24.9 | 1400000
2022-10-10 | 188790 | 118.79 | 7.34 | 7.38 | 139 | 21 | 340 | 40 | 309 | 32 | NA | 600 | 0.2 | 25.1 | 1700000
2022-10-11 | 122140 | 122.14 | 7.33 | 7.36 | 129 | 23 | 304 | 48 | 296 | 32 | NA | 400 | 0.3 | 24.6 | 1300000
2022-10-12 | 109330 | 109.33 | 7.19 | 7.24 | 126 | 21 | 316 | 44 | 303 | 28 | NA | 500 | 0.2 | 25.4 | 1100000
2022-10-13 | 121370 | 121.37 | 7.26 | 7.29 | 133 | 24 | 312 | 48 | 308 | 32 | NA | 700 | 0.3 | 25.3 | 1200000
2022-10-14 | 123970 | 123.97 | 7.29 | 7.34 | 139 | 20 | 348 | 40 | 294 | 27 | NA | 800 | 0.2 | 25.4 | 1100000
2022-10-15 | 128250 | 128.25 | 7.22 | 7.29 | 133 | 21 | 328 | 40 | 302 | 31 | NA | 600 | 0.3 | 25 | 1400000
2022-10-16 | 123140 | 123.14 | 7.26 | 7.34 | 136 | 23 | 336 | 44 | 308 | 27 | NA | 400 | 0.2 | 24.4 | 1300000
2022-10-17 | 118720 | 118.72 | 7.29 | 7.36 | 129 | 22 | 332 | 36 | 305 | 30 | NA | 500 | 0.3 | 24.8 | 1700000
2022-10-18 | 116760 | 116.76 | 7.32 | 7.38 | 126 | 20 | 344 | 40 | 308 | 33 | NA | 800 | 0.2 | 25.2 | 1300000
2022-10-19 | 115730 | 115.73 | 7.27 | 7.31 | 133 | 23 | 328 | 44 | 312 | 30 | NA | 600 | 0.3 | 25.4 | 1200000
2022-10-20 | 122850 | 122.85 | 7.29 | 7.34 | 129 | 20 | 336 | 40 | 302 | 28 | NA | 500 | 0.3 | 25.1 | 1100000
2022-10-21 | 128600 | 128.6 | 7.31 | 7.35 | 136 | 21 | 344 | 44 | 302 | 31 | NA | 400 | 0.2 | 25.1 | 1300000
2022-10-22 | 124680 | 124.68 | 7.26 | 7.35 | 129 | 20 | 334 | 44 | 307 | 32 | NA | 700 | 0.2 | 24.6 | 1400000
2022-10-23 | 124470 | 124.47 | 7.27 | 7.31 | 133 | 22 | 328 | 48 | 306 | 27 | NA | 600 | 0.3 | 25.4 | 1200000
2022-10-24 | 126390 | 126.39 | 7.33 | 7.35 | 136 | 21 | 340 | 40 | 312 | 28 | NA | 700 | 0.2 | 25.3 | 1400000
2022-10-25 | 126890 | 126.89 | 7.29 | 7.36 | 129 | 20 | 340 | 44 | 312 | 30 | NA | 500 | 0.3 | 25.5 | 1700000
2022-10-26 | 127440 | 127.44 | 7.33 | 7.37 | 143 | 24 | 356 | 48 | 302 | 31 | NA | 800 | 0.2 | 24.2 | 1300000
2022-10-27 | 123630 | 123.63 | 7.28 | 7.35 | 129 | 22 | 328 | 44 | 305 | 28 | NA | 600 | 0.3 | 25.1 | 1400000
2022-10-28 | 127130 | 127.13 | 7.31 | 7.36 | 136 | 23 | 344 | 48 | 307 | 30 | NA | 700 | 0.2 | 25.2 | 1300000
2022-10-29 | 120600 | 120.6 | 7.29 | 7.34 | 129 | 21 | 336 | 44 | 310 | 28 | NA | 500 | 0.2 | 24.8 | 1200000
2022-10-30 | 113030 | 113.02 | 7.34 | 7.32 | 126 | 20 | 324 | 40 | 306 | 30 | NA | 400 | 0.3 | 25.1 | 1700000
2022-10-31 | 110160 | 110.16 | 7.33 | 7.39 | 133 | 22 | 340 | 44 | 303 | 27 | NA | 700 | 0.2 | 24.3 | 1100000
Average | 124699.0323 | 120.8181 | 7.2945 | 7.3439 | 131.5484 | 21.4194 | 331.4194 | 43.0968 | 303.6129 | 29.871 | NA | 600 | 0.25484 | 25.1 | 1354838.7097
3745.36
25.032
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 109330 | 109.33 | 7.19 | 7.24 | 123 | 19 | 304 | 36 | 288 | 27 |  | 400 | 0.2 | 24.2 | 1100000
Max | 188790 | 133.47 | 7.34 | 7.39 | 143 | 24 | 356 | 48 | 312 | 35 |  | 800 | 0.4 | 25.7 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-10-01 | 75680 | 75.68 | 7.31 | 7.78 | 123 | 16 | 332 | 40 | 305 | 25 | NA | 700 | 0.2 | 23.93 | 1700000
2022-10-02 | 75260 | 75.26 | 7.42 | 7.69 | 129 | 15 | 316 | 44 | 312 | 24 | NA | 500 | 0.3 | 21.85 | 1400000
2022-10-03 | 74680 | 74.68 | 7.37 | 7.71 | 126 | 15 | 324 | 40 | 295 | 23 | NA | 600 | 0.2 | 22.86 | 1300000
2022-10-04 | 80470 | 80.47 | 7.41 | 7.78 | 130 | 14 | 320 | 44 | 308 | 26 | NA | 700 | 0.3 | 23.27 | 1400000
2022-10-05 | 76730 | 76.73 | 7.35 | 7.79 | 133 | 16 | 328 | 40 | 296 | 24 | NA | 400 | 0.2 | 24.23 | 1300000
2022-10-06 | 79130 | 79.13 | 7.33 | 7.75 | 123 | 15 | 332 | 44 | 287 | 26 | NA | 500 | 0.3 | 24.45 | 1700000
2022-10-07 | 72380 | 72.38 | 7.29 | 7.71 | 129 | 16 | 316 | 36 | 282 | 23 | NA | 400 | 0.2 | 22.62 | 1400000
2022-10-08 | 73900 | 73.9 | 7.36 | 7.78 | 133 | 17 | 340 | 44 | 307 | 28 | NA | 500 | 0.2 | 23.06 | 1700000
2022-10-09 | 71330 | 71.33 | 7.33 | 7.69 | 123 | 18 | 324 | 44 | 284 | 22 | NA | 600 | 0.3 | 24.9 | 1400000
2022-10-10 | 77740 | 77.74 | 7.28 | 7.73 | 119 | 19 | 332 | 36 | 292 | 24 | NA | 400 | 0.2 | 23.21 | 1300000
2022-10-11 | 65700 | 65.7 | 7.47 | 7.62 | 123 | 16 | 340 | 40 | 312 | 28 | NA | 600 | 0.3 | 23.66 | 1700000
2022-10-12 | 73560 | 73.56 | 7.45 | 7.73 | 130 | 18 | 328 | 44 | 276 | 27 | NA | 400 | 0.2 | 25.81 | 1400000
2022-10-13 | 74390 | 74.39 | 7.51 | 7.67 | 136 | 19 | 332 | 40 | 285 | 26 | NA | 500 | 0.2 | 24.16 | 1300000
2022-10-14 | 76060 | 75.06 | 7.38 | 7.65 | 143 | 17 | 316 | 44 | 281 | 28 | NA | 600 | 0.3 | 22.52 | 1700000
2022-10-15 | 73830 | 73.83 | 7.35 | 7.71 | 130 | 18 | 312 | 44 | 273 | 29 | NA | 500 | 0.2 | 23.18 | 1400000
2022-10-16 | 71700 | 71.7 | 7.42 | 7.73 | 136 | 19 | 316 | 40 | 272 | 28 | NA | 400 | 0.2 | 23.63 | 1300000
2022-10-17 | 73960 | 73.96 | 7.37 | 7.71 | 123 | 16 | 336 | 44 | 283 | 29 | NA | 500 | 0.3 | 23.57 | 1400000
2022-10-18 | 73270 | 73.27 | 7.49 | 7.81 | 130 | 18 | 340 | 48 | 276 | 27 | NA | 500 | 0.2 | 22.25 | 1700000
2022-10-19 | 70820 | 70.82 | 7.37 | 7.75 | 136 | 17 | 344 | 44 | 312 | 26 | NA | 600 | 0.3 | 24.67 | 1300000
2022-10-20 | 68220 | 68.22 | 7.42 | 7.73 | 123 | 18 | 344 | 40 | 284 | 24 | NA | 400 | 0.2 | 22.8 | 1400000
2022-10-21 | 69320 | 69.32 | 7.38 | 7.71 | 130 | 16 | 336 | 40 | 293 | 25 | NA | 500 | 0.2 | 24.02 | 1700000
2022-10-22 | 75840 | 75.84 | 7.43 | 7.75 | 126 | 17 | 316 | 36 | 287 | 24 | NA | 600 | 0.3 | 23.21 | 1400000
2022-10-23 | 79590 | 79.59 | 7.39 | 7.79 | 130 | 18 | 312 | 40 | 272 | 26 | NA | 400 | 0.3 | 23.8 | 1300000
2022-10-24 | 76010 | 76.01 | 7.35 | 7.75 | 146 | 16 | 340 | 44 | 308 | 29 | NA | 500 | 0.2 | 23.98 | 1400000
2022-10-25 | 74630 | 74.63 | 7.41 | 7.78 | 133 | 17 | 324 | 40 | 269 | 28 | NA | 400 | 0.2 | 23.21 | 1400000
2022-10-26 | 75990 | 75.99 | 7.38 | 7.73 | 139 | 16 | 316 | 40 | 267 | 24 | NA | 600 | 0.3 | 22.69 | 1700000
2022-10-27 | 75380 | 75.38 | 7.47 | 7.79 | 130 | 17 | 328 | 36 | 265 | 23 | NA | 400 | 0.3 | 23.72 | 1300000
2022-10-28 | 75140 | 75.14 | 7.31 | 7.75 | 126 | 18 | 332 | 44 | 297 | 24 | NA | 500 | 0.2 | 24.99 | 1700000
2022-10-29 | 74890 | 74.89 | 7.46 | 7.74 | 133 | 19 | 336 | 40 | 273 | 25 | NA | 700 | 0.2 | 23.8 | 1400000
2022-10-30 | 71740 | 71.74 | 7.37 | 7.72 | 146 | 17 | 344 | 44 | 267 | 24 | NA | 600 | 0.3 | 22.8 | 1700000
2022-10-31 | 73920 | 73.92 | 7.48 | 7.73 | 130 | 19 | 332 | 40 | 295 | 23 | NA | 500 | 0.2 | 24.85 | 1400000
Average | 74234.1935 | 74.2019 | 7.3906 | 7.7342 | 130.5484 | 17 | 328.6452 | 41.4194 | 287.5806 | 25.5484 | NA | 516.129 | 0.24194 | 23.6032 | 1470967.7419
2300.26
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 65700 | 65.7 | 7.28 | 7.62 | 119 | 14 | 312 | 36 | 265 | 22 |  | 400 | 0.2 | 21.85 | 1300000
Max | 80470 | 80.47 | 7.51 | 7.81 | 146 | 19 | 344 | 48 | 312 | 29 |  | 700 | 0.3 | 25.81 | 1700000