## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-10-01 | 108960 | 108.96 | 7.05 | 7.53 | 140 | 25 | 312 | 42 | 271 | 32 | NA | 500 | 0.3 | 23.6 | 1700000
2023-10-02 | 121340 | 121.34 | 7.09 | 7.43 | 135 | 20 | 308 | 38 | 279 | 35 | NA | 600 | 0.2 | 24 | 1200000
2023-10-03 | 107810 | 107.81 | 7.08 | 7.41 | 130 | 22 | 296 | 44 | 268 | 36 | NA | 700 | 0.3 | 24.22 | 1400000
2023-10-04 | 104150 | 104.15 | 7.19 | 7.46 | 140 | 21 | 302 | 42 | 275 | 35 | NA | 500 | 0.2 | 24.7 | 1300000
2023-10-05 | 105070 | 105.07 | 7.12 | 7.49 | 125 | 20 | 306 | 40 | 269 | 37 | NA | 400 | 0.3 | 24.6 | 1100000
2023-10-06 | 113560 | 113.56 | 7.1 | 7.53 | 135 | 24 | 310 | 42 | 277 | 33 | NA | 600 | 0.3 | 23.8 | 1400000
2023-10-07 | 115910 | 115.91 | 7.18 | 7.57 | 140 | 21 | 312 | 40 | 271 | 35 | NA | 500 | 0.2 | 24.2 | 1300000
2023-10-08 | 117200 | 117.2 | 7.26 | 7.55 | 130 | 20 | 304 | 38 | 280 | 34 | NA | 400 | 0.3 | 23.6 | 1100000
2023-10-09 | 116120 | 116.12 | 7.35 | 7.56 | 125 | 21 | 298 | 42 | 268 | 38 | NA | 700 | 0.2 | 24.2 | 1700000
2023-10-10 | 114390 | 114.39 | 7.36 | 7.59 | 130 | 19 | 293 | 41 | 268 | 39 | NA | 600 | 0.3 | 24.66 | 1200000
2023-10-11 | 80340 | 80.34 | 7.2 | 7.51 | 135 | 24 | 306 | 46 | 266 | 36 | NA | 400 | 0.2 | 24.8 | 1300000 | Naini-I Facility (Naini-I STP, Gaughat MPS & Chacharnala SPS)stopped at 18:50 on 11.10.2023 for the replacement work of flow meter in new header line Gaughat MPS, so the flow is less than the normal flow for 11.10.2023 and O MLD for 12.10.2023 and 13.10.2023. Naini-I Facility is restarted on 14.10.2023 at 00:50
2023-10-12 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | 22.7 | 1100000
2023-10-13 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | 22.8 | 1400000
2023-10-14 | 110500 | 110.5 | 7.41 | 7.5 | 130 | 18 | 305 | 40 | 275 | 37 | NA | 500 | 0.3 | 24.11 | 1300000
2023-10-15 | 112230 | 112.23 | 7.43 | 7.52 | 125 | 19 | 302 | 41 | 278 | 40 | NA | 700 | 0.2 | 24.4 | 1200000
2023-10-16 | 111350 | 111.35 | 7.46 | 7.51 | 130 | 20 | 308 | 42 | 266 | 38 | NA | 400 | 0.3 | 24.46 | 1100000
2023-10-17 | 110850 | 110.85 | 7.33 | 7.49 | 135 | 18 | 298 | 39 | 269 | 36 | NA | 600 | 0.2 | 24.64 | 1400000
2023-10-18 | 111890 | 111.89 | 7.27 | 7.56 | 130 | 20 | 302 | 40 | 278 | 39 | NA | 500 | 0.3 | 24.92 | 1200000
2023-10-19 | 109660 | 109.66 | 7.31 | 7.57 | 125 | 19 | 306 | 42 | 275 | 37 | NA | 700 | 0.3 | 24.41 | 1700000
2023-10-20 | 111480 | 111.48 | 7.29 | 7.61 | 130 | 22 | 294 | 44 | 277 | 40 | NA | 800 | 0.2 | 24.26 | 1300000
2023-10-21 | 110240 | 110.24 | 7.21 | 7.58 | 135 | 18 | 300 | 42 | 265 | 38 | NA | 600 | 0.3 | 24.7 | 1100000
2023-10-22 | 112150 | 112.15 | 7.11 | 7.62 | 140 | 23 | 312 | 44 | 271 | 40 | NA | 700 | 0.2 | 24.46 | 1400000
2023-10-23 | 116370 | 116.37 | 7.14 | 7.6 | 130 | 21 | 296 | 42 | 268 | 39 | NA | 500 | 0.3 | 23.87 | 1100000
2023-10-24 | 119080 | 119.08 | 7.17 | 7.64 | 125 | 19 | 300 | 40 | 273 | 38 | NA | 600 | 0.3 | 24.33 | 1400000
2023-10-25 | 113680 | 113.68 | 7.19 | 7.61 | 135 | 20 | 303 | 42 | 270 | 35 | NA | 400 | 0.2 | 24.24 | 1300000
2023-10-26 | 115370 | 115.37 | 7.17 | 7.62 | 125 | 19 | 286 | 39 | 279 | 40 | NA | 600 | 0.3 | 24.7 | 1700000
2023-10-27 | 114360 | 114.36 | 7.16 | 7.63 | 120 | 18 | 309 | 41 | 281 | 38 | NA | 400 | 0.2 | 24.2 | 1100000
2023-10-28 | 115790 | 115.79 | 7.13 | 7.61 | 130 | 19 | 304 | 40 | 276 | 37 | NA | 500 | 0.3 | 24.37 | 1200000
2023-10-29 | 114880 | 114.88 | 7.21 | 7.59 | 135 | 22 | 288 | 43 | 272 | 38 | NA | 800 | 0.2 | 24.2 | 1700000
2023-10-30 | 110700 | 110.7 | 7.17 | 7.57 | 130 | 21 | 302 | 46 | 274 | 39 | NA | 700 | 0.3 | 24.44 | 1400000
2023-10-31 | 112340 | 112.34 | 7.13 | 7.69 | 135 | 19 | 296 | 43 | 268 | 40 | NA | 600 | 0.2 | 24.2 | 1300000
Average | 104444.1935 | 104.4442 | 7.2162 | 7.5569 | 131.3793 | 20.4138 | 302 | 41.5517 | 272.6552 | 37.2069 | NA | 568.9655 | 0.25517 | 24.219 | 1325806.4516
3237.77
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.05 | 7.41 | 120 | 18 | 286 | 38 | 265 | 32 |  | 400 | 0.2 | 22.7 | 1100000
Max | 121340 | 121.34 | 7.46 | 7.69 | 140 | 25 | 312 | 46 | 281 | 40 |  | 800 | 0.3 | 24.92 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-10-01 | 83190 | 83.19 | 6.98 | 7.56 | 120 | 15 | 296 | 40 | 258 | 25 | NA | 400 | 0.3 | 23.42 | 1300000
2023-10-02 | 83710 | 83.71 | 7.09 | 7.55 | 130 | 18 | 300 | 44 | 256 | 26 | NA | 500 | 0.2 | 23.02 | 1700000
2023-10-03 | 82210 | 82.21 | 7.13 | 7.58 | 125 | 17 | 296 | 40 | 262 | 23 | NA | 600 | 0.3 | 23.23 | 1300000
2023-10-04 | 78180 | 78.18 | 7.12 | 7.62 | 120 | 16 | 292 | 44 | 269 | 26 | NA | 700 | 0.2 | 24.68 | 1400000
2023-10-05 | 76300 | 76.3 | 7.08 | 7.63 | 130 | 17 | 304 | 40 | 272 | 25 | NA | 500 | 0.3 | 23.42 | 1700000
2023-10-06 | 80710 | 80.71 | 7.15 | 7.62 | 135 | 18 | 300 | 48 | 266 | 27 | NA | 600 | 0.2 | 24.56 | 1400000
2023-10-07 | 72740 | 72.74 | 7.17 | 7.57 | 130 | 17 | 296 | 44 | 263 | 28 | NA | 700 | 0.3 | 23.42 | 1700000
2023-10-08 | 84540 | 84.54 | 7.16 | 7.61 | 125 | 16 | 292 | 40 | 261 | 26 | NA | 400 | 0.2 | 24.64 | 1300000
2023-10-09 | 73810 | 77.62 | 7.13 | 7.65 | 140 | 18 | 288 | 44 | 259 | 25 | NA | 500 | 0.3 | 23.11 | 1400000
2023-10-10 | 80220 | 80.22 | 7.15 | 7.62 | 125 | 17 | 296 | 44 | 262 | 27 | NA | 600 | 0.3 | 23.79 | 1700000
2023-10-11 | 76840 | 76.84 | 7.14 | 7.6 | 130 | 16 | 300 | 40 | 267 | 25 | NA | 400 | 0.2 | 24.74 | 1300000
2023-10-12 | 78260 | 78.26 | 7.16 | 7.65 | 120 | 17 | 296 | 44 | 263 | 24 | NA | 700 | 0.3 | 24.97 | 1700000
2023-10-13 | 79860 | 79.86 | 7.14 | 7.62 | 125 | 16 | 288 | 40 | 259 | 23 | NA | 500 | 0.3 | 23.4 | 1400000
2023-10-14 | 77080 | 77.08 | 7.17 | 7.61 | 130 | 17 | 292 | 44 | 257 | 25 | NA | 400 | 0.2 | 23.42 | 1300000
2023-10-15 | 81500 | 81.5 | 7.15 | 7.6 | 120 | 15 | 296 | 44 | 264 | 23 | NA | 600 | 0.3 | 23.16 | 1700000
2023-10-16 | 78130 | 78.13 | 7.16 | 7.59 | 135 | 18 | 288 | 48 | 285 | 25 | NA | 400 | 0.3 | 24.53 | 1400000
2023-10-17 | 78240 | 78.24 | 7.18 | 7.62 | 140 | 17 | 292 | 44 | 265 | 24 | NA | 500 | 0.2 | 23.17 | 1200000
2023-10-18 | 79010 | 79.01 | 7.25 | 7.64 | 130 | 16 | 296 | 40 | 258 | 25 | NA | 600 | 0.3 | 24.79 | 1300000
2023-10-19 | 80050 | 80.05 | 7.26 | 7.67 | 125 | 17 | 292 | 48 | 256 | 24 | NA | 400 | 0.3 | 23.41 | 1700000
2023-10-20 | 79870 | 79.87 | 7.22 | 7.64 | 130 | 16 | 300 | 40 | 263 | 25 | NA | 700 | 0.2 | 23.06 | 1400000
2023-10-21 | 81520 | 81.52 | 7.23 | 7.66 | 135 | 18 | 296 | 44 | 259 | 26 | NA | 600 | 0.3 | 23.78 | 1700000
2023-10-22 | 79910 | 79.91 | 7.26 | 7.65 | 140 | 17 | 304 | 40 | 268 | 27 | NA | 500 | 0.3 | 23.4 | 1300000
2023-10-23 | 80020 | 80.02 | 7.27 | 7.7 | 145 | 18 | 296 | 48 | 263 | 24 | NA | 400 | 0.2 | 22.73 | 1200000
2023-10-24 | 80780 | 80.78 | 7.25 | 7.69 | 130 | 16 | 292 | 40 | 258 | 23 | NA | 600 | 0.2 | 23.38 | 1400000
2023-10-25 | 81040 | 81.04 | 7.26 | 7.67 | 135 | 18 | 304 | 44 | 271 | 26 | NA | 500 | 0.3 | 23.34 | 1700000
2023-10-26 | 79190 | 79.19 | 7.25 | 7.66 | 130 | 16 | 296 | 40 | 264 | 25 | NA | 400 | 0.3 | 24.75 | 1300000
2023-10-27 | 80430 | 80.43 | 7.26 | 7.72 | 125 | 17 | 288 | 44 | 257 | 26 | NA | 600 | 0.2 | 23.35 | 1700000
2023-10-28 | 79980 | 79.98 | 7.29 | 7.69 | 130 | 16 | 292 | 40 | 261 | 25 | NA | 700 | 0.3 | 23.24 | 1400000
2023-10-29 | 81990 | 81.99 | 7.24 | 7.72 | 125 | 15 | 300 | 40 | 269 | 24 | NA | 500 | 0.2 | 24.53 | 1300000
2023-10-30 | 82820 | 82.82 | 7.25 | 7.73 | 135 | 18 | 304 | 44 | 271 | 26 | NA | 400 | 0.3 | 23.83 | 1400000
2023-10-31 | 80790 | 80.79 | 7.21 | 7.75 | 130 | 17 | 296 | 40 | 265 | 27 | NA | 600 | 0.3 | 24.25 | 1700000
Average | 79771.6129 | 79.8945 | 7.1858 | 7.6416 | 129.8387 | 16.7742 | 295.7419 | 42.7097 | 263.5806 | 25.1613 | NA | 532.2581 | 0.26129 | 23.7587 | 1464516.129
2476.73
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 72740 | 72.74 | 6.98 | 7.55 | 120 | 15 | 288 | 40 | 256 | 23 |  | 400 | 0.2 | 22.73 | 1200000
Max | 84540 | 84.54 | 7.29 | 7.75 | 145 | 18 | 304 | 48 | 285 | 28 |  | 700 | 0.3 | 24.97 | 1700000