## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-09-01 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | - | 1. Outlet gate for the effluent of STP was closed and bypass gate of Naini-I STP was opened at 10:00 PM on 25.08.2022. 2. Gaughat MPS is in operation but raw sewage pumped from it is bypassed before Naini-I STP on 25.08.2022. 3. Chacharnalla SPS is in operation but raw sewage pumped from it is bypassed before Gaughat MPS on 25.08.2022. 4. Currently, no sewage is coming to Naini-I STP.
2022-09-02 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2022-09-03 | 34800 | 34.8 | - | - | - | - | - | - | - | - | NA | - | - | - | - | 1. Bypass gate was closed and Sewage was taken inside STP at 6:00 PM on 03.09.2022 as water level in river Yamuna has gone down. 2. Expansion bellow in old rising main from Gaughat MPS to Naini-I STP is broken at 3:30 PM on 03.09.2022. Maintenance work is in progress. 3. Currently raw sewage is being transferred from Gaughat MPS to Naini-I STP through new line. 4. KPI testing was not done since composite sample was not available.
2022-09-04 | 102920 | 102.92 | 7.28 | 7.32 | 119 | 75 | 308 | 144 | 280 | 132 | NA | - | - | - | - | 1. 100% treatment of STP is not started since the installation of equipment is in progress. 2. Replacement work for broken expansion bellow in old rising main from Gaughat MPS to Naini-I STP is in progress. 3. KPIs are out of range since the new culture is being developed inside the units after starting the operation of STP.
2022-09-05 | 115660 | 115.66 | 7.29 | 7.35 | 123 | 55 | 316 | 88 | 292 | 78 | NA | - | - | 25.4 | 1400000
2022-09-06 | 124520 | 124.52 | 7.33 | 7.36 | 126 | 50 | 328 | 68 | 294 | 64 | NA | 800 | 0.2 | 25.2 | 1700000 | 1. 100% treatment of STP is started inside the STP. 2. Replacement work for broken expansion bellow in old rising main from Gaughat MPS to Naini-I STP is in progress. 3. KPIs are out of range since the new culture is being developed inside the units after starting the operation of STP.
2022-09-07 | 112500 | 112.5 | 7.28 | 7.38 | 129 | 40 | 320 | 52 | 298 | 52 | NA | 700 | 0.4 | 25.2 | 1300000 | 1. Replacement work for broken expansion bellow in old rising main from Gaughat MPS to Naini-I STP is in progress. 2. KPIs are out of range since the new culture is being developed inside the units after starting the operation of STP.
2022-09-08 | 110350 | 110.35 | 7.31 | 7.37 | 136 | 33 | 332 | 48 | 296 | 46 | NA | 600 | 0.4 | 25.5 | 1200000
2022-09-09 | 110900 | 110.9 | 7.28 | 7.33 | 139 | 29 | 344 | 44 | 288 | 42 | NA | 500 | 0.3 | 25.2 | 1200000 | Replacement work for broken expansion bellow in old rising main from Gaughat MPS to Naini-I STP is in progress.
2022-09-10 | 107210 | 107.21 | 7.33 | 7.37 | 129 | 26 | 332 | 40 | 296 | 35 | NA | 400 | 0.3 | 25.3 | 1400000
2022-09-11 | 108110 | 108.11 | 7.28 | 7.35 | 126 | 22 | 320 | 36 | 312 | 37 | NA | 600 | 0.3 | 25.14 | 1300000
2022-09-12 | 107940 | 107.94 | 7.33 | 7.39 | 129 | 20 | 328 | 40 | 303 | 34 | NA | 700 | 0.4 | 25.3 | 1200000
2022-09-13 | 111990 | 111.99 | 7.31 | 7.36 | 126 | 23 | 304 | 44 | 294 | 36 | NA | 500 | 0.4 | 25.2 | 1400000 | 1. Replacement work for broken expansion bellow in old rising main from Gaughat MPS to Naini-I STP is completed at 8:00 PM on 12.09.2022. 2. Both rising mains from Gaughat MPS to Naini-I STP are started at 11:00 AM on 13.09.2022. Currently raw sewage is being transferred from both rising mains.
2022-09-14 | 128170 | 128.17 | 7.34 | 7.39 | 119 | 20 | 296 | 40 | 296 | 35 | NA | 400 | 0.3 | 25.4 | 1700000
2022-09-15 | 122610 | 122.61 | 7.58 | 7.48 | 123 | 23 | 304 | 48 | 302 | 34 | NA | 500 | 0.3 | 25.4 | 1300000
2022-09-16 | 126740 | 126.74 | 7.28 | 7.35 | 119 | 22 | 308 | 40 | 294 | 32 | NA | 700 | 0.3 | 25.2 | 1400000
2022-09-17 | 112520 | 112.52 | 7.33 | 7.38 | 126 | 23 | 312 | 44 | 303 | 35 | NA | 800 | 0.2 | 25.3 | 1700000
2022-09-18 | 125510 | 125.51 | 7.28 | 7.35 | 123 | 22 | 324 | 48 | 308 | 33 | NA | 600 | 0.3 | 25.6 | 1300000
2022-09-19 | 117210 | 117.21 | 7.36 | 7.39 | 126 | 21 | 308 | 44 | 304 | 36 | NA | 500 | 0.3 | 25.6 | 1200000
2022-09-20 | 146410 | 146.41 | 7.34 | 7.42 | 123 | 20 | 304 | 40 | 286 | 34 | NA | 400 | 0.3 | 25.1 | 1700000
2022-09-21 | 120480 | 120.48 | 7.39 | 7.48 | 119 | 23 | 292 | 44 | 288 | 27 | NA | 600 | 0.4 | 25.6 | 1400000
2022-09-22 | 119610 | 119.61 | 7.44 | 7.52 | 126 | 24 | 308 | 48 | 288 | 30 | NA | 500 | 0.3 | 25.4 | 1300000
2022-09-23 | 118980 | 118.98 | 7.36 | 7.39 | 129 | 22 | 324 | 44 | 303 | 33 | NA | 700 | 0.3 | 24.9 | 1200000
2022-09-24 | 120320 | 120.32 | 7.33 | 7.41 | 136 | 20 | 340 | 40 | 301 | 30 | NA | 800 | 0.2 | 25.2 | 1400000
2022-09-25 | 125130 | 125.13 | 7.36 | 7.46 | 136 | 23 | 344 | 48 | 296 | 32 | NA | 500 | 0.3 | 25.4 | 1100000
2022-09-26 | 121540 | 121.54 | 7.33 | 7.44 | 139 | 20 | 348 | 40 | 304 | 31 | NA | 700 | 0.4 | 25.3 | 1700000
2022-09-27 | 116860 | 116.86 | 7.28 | 7.38 | 133 | 24 | 336 | 44 | 306 | 32 | NA | 600 | 0.3 | 25.2 | 1300000
2022-09-28 | 121270 | 121.27 | 7.29 | 7.34 | 139 | 20 | 344 | 40 | 308 | 30 | NA | 400 | 0.2 | 25.3 | 1400000
2022-09-29 | 121150 | 121.15 | 7.28 | 7.36 | 129 | 22 | 336 | 44 | 306 | 28 | NA | 500 | 0.3 | 25 | 1200000
2022-09-30 | 126010 | 126.01 | 7.31 | 7.34 | 136 | 24 | 348 | 48 | 309 | 32 | NA | 700 | 0.2 | 25.6 | 1300000
Average | 107914 | 107.914 | 7.3296 | 7.3874 | 128.2593 | 27.6296 | 322.5185 | 49.9259 | 298.3333 | 40.7407 | NA | 588 | 0.304 | 25.3054 | 1373076.9231
3237.42
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.28 | 7.32 | 119 | 20 | 292 | 36 | 280 | 27 |  | 400 | 0.2 | 24.9 | 1100000
Max | 146410 | 146.41 | 7.58 | 7.52 | 139 | 75 | 348 | 144 | 312 | 132 |  | 800 | 0.4 | 25.6 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2022-09-01 | 13970 | 13.97 | 7.39 | 7.75 | 65 | 10 | 108 | 20 | 79 | 15 | NA | - | - | - | - | 1. Inlet gate at tapping point for nearby drain of Rajapur SPS was closed at around 1:00 PM on 18.08.2022 due to rise in water level of Ganga river due to flood. 2. Mumfordganj SPS was in operation but scour valve in rising main was opened at 9:30 AM on 19.08.2022 for bypassing sewage as Rajapur STP was not in operation due to flood. 3. Currently, raw sewage due to leakage in inlet valve and seepage of water through ground due to flood is coming in STP.
2022-09-02 | 7630 | 7.63 | 7.28 | 7.73 | 60 | 12 | 96 | 24 | 76 | 14 | NA | - | - | - | -
2022-09-03 | 53560 | 53.56 | 7.35 | 7.69 | 125 | 16 | 316 | 36 | 275 | 23 | NA | 700 | 0.2 | - | - | 1. Outlet Gate of Rajapur STP was opened at 10:00 AM on 03.09.2022 after fall of river level in river. 2. Scour valve in rising main from Mumfordganj SPS to Rajapur STP is closed 12:30 PM on 03.09.2022 after fall of river level in river. Now complete sewage form Mumfordganj SPS is being transferred to Rajapur STP.
2022-09-04 | 71220 | 71.22 | 7.43 | 7.77 | 130 | 18 | 324 | 40 | 286 | 25 | NA | 800 | 0.2 | - | - | Removal of sand bags from Tapping point of Rajapur SPS are in progress. Therefore, sewage received from Rajapur SPS is low.
2022-09-05 | 72090 | 72.09 | 7.39 | 7.78 | 140 | 16 | 332 | 36 | 292 | 27 | NA | 600 | 0.3 | - | -
2022-09-06 | 72960 | 72.96 | 7.42 | 7.75 | 135 | 18 | 340 | 44 | 305 | 26 | NA | 700 | 0.2 | - | -
2022-09-07 | 70650 | 70.65 | 7.39 | 7.67 | 130 | 17 | 360 | 36 | 298 | 28 | NA | 600 | 0.3 | 24.97 | 1700000
2022-09-08 | 72370 | 72.37 | 7.35 | 7.71 | 140 | 16 | 344 | 40 | 295 | 25 | NA | 700 | 0.2 | 23.45 | 1400000
2022-09-09 | 73160 | 73.16 | 7.28 | 7.65 | 135 | 17 | 348 | 44 | 287 | 27 | NA | 700 | 0.2 | 24.53 | 1400000
2022-09-10 | 74090 | 74.09 | 7.35 | 7.68 | 120 | 15 | 340 | 40 | 293 | 24 | NA | 600 | 0.3 | 25.37 | 1700000
2022-09-11 | 76850 | 76.85 | 7.32 | 7.71 | 130 | 16 | 320 | 36 | 306 | 23 | NA | 500 | 0.2 | 24.63 | 1400000
2022-09-12 | 83950 | 83.95 | 7.35 | 7.73 | 125 | 18 | 344 | 40 | 298 | 26 | NA | 700 | 0.3 | 24.57 | 1700000 | Removal of sand bags from Tapping point of Rajapur SPS is completed. Sluice gate is opened at 12:15 PM on 12.09.2022. Now complete sewage is coming inside the STP.
2022-09-13 | 81180 | 81.18 | 7.37 | 7.75 | 135 | 17 | 340 | 36 | 287 | 25 | NA | 600 | 0.2 | 25.15 | 1200000
2022-09-14 | 83370 | 83.37 | 7.34 | 7.72 | 140 | 18 | 332 | 40 | 295 | 24 | NA | 500 | 0.2 | 23.78 | 1400000
2022-09-15 | 82950 | 82.95 | 7.13 | 7.76 | 130 | 15 | 320 | 36 | 294 | 25 | NA | 600 | 0.3 | 22.57 | 1700000
2022-09-16 | 84950 | 84.95 | 7.25 | 7.69 | 130 | 16 | 336 | 44 | 276 | 23 | NA | 500 | 0.2 | 24.28 | 1400000
2022-09-17 | 79840 | 79.84 | 7.29 | 7.77 | 135 | 18 | 328 | 40 | 281 | 26 | NA | 700 | 0.2 | 25.32 | 1700000
2022-09-18 | 80020 | 80.02 | 7.32 | 7.76 | 125 | 16 | 332 | 36 | 293 | 25 | NA | 600 | 0.2 | 22.87 | 1400000
2022-09-19 | 79110 | 79.11 | 7.37 | 7.75 | 130 | 17 | 324 | 44 | 272 | 23 | NA | 600 | 0.3 | 23.96 | 1300000
2022-09-20 | 75820 | 75.82 | 7.28 | 7.69 | 135 | 16 | 332 | 40 | 287 | 25 | NA | 500 | 0.3 | 22.35 | 1400000
2022-09-21 | 80740 | 80.74 | 7.35 | 7.77 | 140 | 17 | 328 | 36 | 276 | 24 | NA | 400 | 0.2 | 24.37 | 1300000
2022-09-22 | 76830 | 76.83 | 7.29 | 7.72 | 125 | 16 | 336 | 40 | 296 | 27 | NA | 700 | 0.2 | 23.21 | 1700000
2022-09-23 | 76320 | 76.32 | 7.33 | 7.68 | 130 | 18 | 324 | 44 | 281 | 26 | NA | 600 | 0.3 | 22.85 | 1400000
2022-09-24 | 79090 | 79.09 | 7.27 | 7.73 | 135 | 16 | 332 | 40 | 279 | 25 | NA | 500 | 0.2 | 23.63 | 1300000
2022-09-25 | 75340 | 75.34 | 7.32 | 7.76 | 140 | 17 | 320 | 36 | 297 | 24 | NA | 400 | 0.2 | 23.21 | 1200000
2022-09-26 | 76260 | 76.26 | 7.28 | 7.72 | 125 | 15 | 336 | 40 | 283 | 28 | NA | 600 | 0.2 | 23.65 | 1400000
2022-09-27 | 72850 | 72.85 | 7.23 | 7.68 | 120 | 16 | 332 | 44 | 311 | 25 | NA | 500 | 0.3 | 23.3 | 1700000
2022-09-28 | 75910 | 75.91 | 7.35 | 7.73 | 130 | 18 | 328 | 40 | 293 | 26 | NA | 700 | 0.2 | 23.6 | 1400000
2022-09-29 | 74710 | 74.71 | 7.27 | 7.65 | 125 | 16 | 324 | 36 | 285 | 24 | NA | 600 | 0.3 | 24.17 | 1700000
2022-09-30 | 77520 | 77.52 | 7.33 | 7.76 | 130 | 17 | 336 | 36 | 298 | 26 | NA | 500 | 0.3 | 23.73 | 1300000
Average | 71843.6667 | 71.8437 | 7.3223 | 7.7237 | 126.5 | 16.2667 | 317.0667 | 38.1333 | 275.8 | 24.4667 | NA | 596.4286 | 0.23929 | 23.8967 | 1466666.6667
2155.31
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 7630 | 7.63 | 7.13 | 7.65 | 60 | 10 | 96 | 20 | 76 | 14 |  | 400 | 0.2 | 22.35 | 1200000
Max | 84950 | 84.95 | 7.43 | 7.78 | 140 | 18 | 360 | 44 | 311 | 28 |  | 800 | 0.3 | 25.37 | 1700000