## Naini-1
Naini-I STP, 80 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 80 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-09-01 | 112870 | 112.87 | 7.25 | 7.41 | 130 | 25 | 314 | 43 | 286 | 35 | NA | 600 | 0.2 | 24.27 | 1200000
2023-09-02 | 117080 | 117.08 | 7.16 | 7.48 | 125 | 24 | 304 | 40 | 276 | 37 | NA | 500 | 0.3 | 23.85 | 1700000
2023-09-03 | 119700 | 119.7 | 7.22 | 7.54 | 120 | 25 | 316 | 38 | 265 | 35 | NA | 400 | 0.2 | 22.94 | 1400000
2023-09-04 | 118630 | 118.63 | 7.19 | 7.43 | 125 | 23 | 296 | 40 | 278 | 37 | NA | 500 | 0.2 | 24.11 | 1300000
2023-09-05 | 124720 | 124.72 | 7.26 | 7.47 | 130 | 24 | 306 | 38 | 261 | 36 | NA | 600 | 0.3 | 23.45 | 1200000
2023-09-06 | 123000 | 123 | 7.15 | 7.5 | 120 | 26 | 310 | 40 | 270 | 38 | NA | 700 | 0.2 | 22.53 | 1400000
2023-09-07 | 124630 | 124.63 | 7.12 | 7.43 | 125 | 23 | 292 | 42 | 263 | 34 | NA | 500 | 0.3 | 23.08 | 1200000
2023-09-08 | 113610 | 113.61 | 7.14 | 7.49 | 135 | 22 | 302 | 40 | 253 | 36 | NA | 600 | 0.3 | 23.37 | 1200000
2023-09-09 | 110530 | 110.53 | 7.08 | 7.55 | 135 | 25 | 294 | 38 | 268 | 35 | NA | 400 | 0.2 | 24.15 | 1400000
2023-09-10 | 113470 | 113.47 | 7.28 | 7.51 | 120 | 22 | 296 | 37 | 278 | 34 | NA | 800 | 0.3 | 24.62 | 1700000
2023-09-11 | 110870 | 110.87 | 7.36 | 7.49 | 120 | 23 | 284 | 38 | 272 | 34 | NA | 600 | 0.2 | 24.6 | 1200000
2023-09-12 | 119220 | 119.22 | 7.46 | 7.51 | 115 | 25 | 292 | 40 | 278 | 38 | NA | 500 | 0.3 | 24.4 | 1300000
2023-09-13 | 105070 | 105.07 | 7.44 | 7.58 | 120 | 22 | 300 | 42 | 282 | 34 | NA | 700 | 0.2 | 24.2 | 1100000
2023-09-14 | 108790 | 108.79 | 7.41 | 7.59 | 115 | 24 | 306 | 44 | 273 | 36 | NA | 600 | 0.3 | 24.51 | 1400000
2023-09-15 | 109750 | 109.75 | 7.44 | 7.51 | 120 | 21 | 312 | 43 | 291 | 33 | NA | 400 | 0.2 | 24.6 | 1200000
2023-09-16 | 110090 | 110.09 | 7.4 | 7.47 | 120 | 13 | 308 | 40 | 278 | 34 | NA | 800 | 0.2 | 23.5 | 1700000
2023-09-17 | 117790 | 117.79 | 7.29 | 7.51 | 115 | 16 | 324 | 41 | 324 | 38 | NA | 600 | 0.3 | 24.65 | 1300000
2023-09-18 | 117830 | 117.83 | 7.33 | 7.52 | 135 | 17 | 308 | 44 | 302 | 40 | NA | 700 | 0.2 | 24.55 | 1200000
2023-09-19 | 106500 | 106.5 | 7.49 | 7.53 | 125 | 19 | 296 | 36 | 274 | 35 | NA | 700 | 0.3 | 24.1 | 1100000
2023-09-20 | 108510 | 108.51 | 7.47 | 7.51 | 140 | 23 | 312 | 42 | 275 | 36 | NA | 500 | 0.2 | 24.57 | 1400000
2023-09-21 | 108400 | 108.4 | 7.49 | 7.52 | 130 | 20 | 316 | 40 | 272 | 37 | NA | 600 | 0.3 | 24.9 | 1300000
2023-09-22 | 109020 | 109.02 | 7.46 | 7.56 | 140 | 18 | 300 | 36 | 268 | 34 | NA | 500 | 0.2 | 25 | 1400000
2023-09-23 | 110730 | 110.73 | 7.56 | 7.59 | 130 | 19 | 308 | 40 | 279 | 36 | NA | 800 | 0.3 | 24.7 | 1700000
2023-09-24 | 108950 | 108.95 | 7.49 | 7.57 | 135 | 23 | 296 | 42 | 270 | 34 | NA | 400 | 0.2 | 24.2 | 1100000
2023-09-25 | 110550 | 110.55 | 7.46 | 7.58 | 140 | 25 | 304 | 44 | 274 | 33 | NA | 600 | 0.3 | 24.9 | 1400000
2023-09-26 | 108980 | 108.98 | 7.28 | 7.55 | 135 | 21 | 312 | 40 | 268 | 38 | NA | 700 | 0.2 | 24.8 | 1300000
2023-09-27 | 101950 | 101.95 | 7.31 | 7.56 | 130 | 24 | 296 | 43 | 270 | 35 | NA | 500 | 0.3 | 24.1 | 1200000
2023-09-28 | 114080 | 114.08 | 7.19 | 7.49 | 140 | 20 | 308 | 40 | 279 | 37 | NA | 400 | 0.3 | 23.87 | 1400000
2023-09-29 | 104260 | 104.26 | 7.21 | 7.51 | 125 | 19 | 300 | 42 | 275 | 33 | NA | 600 | 0.2 | 24.2 | 1700000
2023-09-30 | 112670 | 112.67 | 7.08 | 7.43 | 145 | 23 | 316 | 44 | 280 | 35 | NA | 800 | 0.3 | 24.8 | 1100000
Average | 112741.6667 | 112.7417 | 7.3157 | 7.513 | 128 | 21.8 | 304.2667 | 40.5667 | 276.0667 | 35.5667 | NA | 586.6667 | 0.25 | 24.184 | 1340000
3382.25
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 101950 | 101.95 | 7.08 | 7.41 | 115 | 13 | 284 | 36 | 253 | 33 |  | 400 | 0.2 | 22.53 | 1100000
Max | 124720 | 124.72 | 7.56 | 7.59 | 145 | 26 | 324 | 44 | 324 | 40 |  | 800 | 0.3 | 25 | 1700000

## Rajapur
Rajapur STP, 60 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 60 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <30 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | FinalTSS (Design - <50 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-09-01 | 65890 | 65.89 | 7.23 | 7.45 | 130 | 17 | 308 | 40 | 287 | 25 | NA | 600 | 0.3 | 23.34 | 1300000
2023-09-02 | 65290 | 65.29 | 7.25 | 7.44 | 125 | 16 | 312 | 44 | 291 | 24 | NA | 400 | 0.2 | 23.16 | 1200000
2023-09-03 | 75780 | 75.78 | 7.15 | 7.29 | 140 | 18 | 324 | 44 | 295 | 23 | NA | 600 | 0.3 | 23.18 | 1700000
2023-09-04 | 77410 | 77.41 | 7.23 | 7.49 | 130 | 17 | 296 | 40 | 259 | 24 | NA | 500 | 0.3 | 24.18 | 1400000
2023-09-05 | 74870 | 74.87 | 7.17 | 7.59 | 125 | 16 | 304 | 44 | 285 | 25 | NA | 700 | 0.3 | 23.22 | 1300000
2023-09-06 | 75430 | 75.43 | 7.12 | 7.62 | 135 | 17 | 292 | 40 | 271 | 23 | NA | 400 | 0.2 | 24.15 | 1200000
2023-09-07 | 79840 | 79.84 | 7.08 | 7.63 | 140 | 18 | 312 | 44 | 289 | 24 | NA | 600 | 0.3 | 23.11 | 1700000
2023-09-08 | 78610 | 78.61 | 7.05 | 7.54 | 130 | 16 | 316 | 40 | 283 | 25 | NA | 500 | 0.3 | 22.98 | 1300000
2023-09-09 | 78880 | 78.88 | 7.14 | 7.55 | 135 | 17 | 308 | 44 | 278 | 24 | NA | 700 | 0.2 | 23.41 | 1400000
2023-09-10 | 87540 | 87.54 | 7.09 | 7.47 | 125 | 16 | 304 | 40 | 272 | 23 | NA | 600 | 0.3 | 23.13 | 1300000
2023-09-11 | 77160 | 77.16 | 7.57 | 7.82 | 115 | 15 | 292 | 44 | 240 | 17 | NA | 400 | 0.2 | 23.54 | 1300000
2023-09-12 | 79830 | 79.83 | 7.18 | 7.6 | 125 | 16 | 296 | 40 | 265 | 22 | NA | 600 | 0.3 | 24.61 | 1700000
2023-09-13 | 82070 | 82.07 | 7.29 | 7.73 | 135 | 18 | 312 | 44 | 245 | 23 | NA | 500 | 0.3 | 23.75 | 1400000
2023-09-14 | 81340 | 81.34 | 7.32 | 7.71 | 125 | 17 | 328 | 40 | 274 | 25 | NA | 600 | 0.2 | 24.32 | 1300000
2023-09-15 | 77100 | 77.1 | 7.24 | 7.53 | 130 | 16 | 324 | 44 | 281 | 24 | NA | 400 | 0.3 | 23.28 | 1700000
2023-09-16 | 82360 | 82.36 | 7.21 | 7.51 | 135 | 17 | 332 | 44 | 305 | 25 | NA | 500 | 0.2 | 23.34 | 1400000
2023-09-17 | 83400 | 83.4 | 7.23 | 7.55 | 130 | 16 | 328 | 40 | 295 | 24 | NA | 600 | 0.3 | 24.22 | 1700000
2023-09-18 | 84840 | 84.84 | 7.25 | 7.43 | 125 | 17 | 324 | 44 | 289 | 23 | NA | 400 | 0.3 | 23.22 | 1300000
2023-09-19 | 80240 | 80.24 | 7.22 | 7.48 | 120 | 16 | 316 | 40 | 274 | 24 | NA | 600 | 0.3 | 23.65 | 1400000
2023-09-20 | 79530 | 79.53 | 7.24 | 7.5 | 125 | 17 | 328 | 44 | 282 | 25 | NA | 500 | 0.2 | 24.52 | 1700000
2023-09-21 | 79250 | 79.25 | 7.29 | 7.51 | 115 | 16 | 332 | 44 | 304 | 24 | NA | 700 | 0.3 | 23.22 | 1400000
2023-09-22 | 79280 | 79.28 | 7.32 | 7.58 | 135 | 17 | 340 | 40 | 317 | 26 | NA | 600 | 0.2 | 22.39 | 1200000
2023-09-23 | 75140 | 75.14 | 7.35 | 7.6 | 120 | 16 | 344 | 44 | 323 | 23 | NA | 400 | 0.3 | 24.49 | 1300000
2023-09-24 | 75640 | 75.64 | 7.32 | 7.63 | 130 | 17 | 292 | 40 | 273 | 24 | NA | 500 | 0.3 | 23.5 | 1700000
2023-09-25 | 77970 | 77.97 | 7.37 | 7.62 | 115 | 16 | 296 | 44 | 271 | 25 | NA | 600 | 0.2 | 24.57 | 1400000
2023-09-26 | 76640 | 76.64 | 7.41 | 7.6 | 125 | 17 | 292 | 40 | 269 | 26 | NA | 400 | 0.3 | 23.35 | 1200000
2023-09-27 | 75480 | 75.48 | 7.42 | 7.53 | 115 | 16 | 296 | 44 | 275 | 25 | NA | 600 | 0.3 | 24.97 | 1700000
2023-09-28 | 80190 | 80.19 | 7.41 | 7.59 | 130 | 18 | 300 | 40 | 268 | 26 | NA | 500 | 0.2 | 23.09 | 1300000
2023-09-29 | 80140 | 80.14 | 7.31 | 7.62 | 115 | 16 | 288 | 40 | 259 | 27 | NA | 700 | 0.3 | 23.67 | 1700000
2023-09-30 | 78450 | 78.45 | 7.13 | 7.61 | 125 | 17 | 292 | 44 | 265 | 25 | NA | 600 | 0.2 | 24.15 | 1400000
Average | 78186.3333 | 78.1863 | 7.253 | 7.5607 | 126.8333 | 16.6333 | 310.9333 | 42.1333 | 279.4667 | 24.1 | NA | 543.3333 | 0.26333 | 23.657 | 1433333.3333
2345.59
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 65290 | 65.29 | 7.05 | 7.29 | 115 | 15 | 288 | 40 | 240 | 17 |  | 400 | 0.2 | 22.39 | 1200000
Max | 87540 | 87.54 | 7.57 | 7.82 | 140 | 18 | 344 | 44 | 323 | 27 |  | 700 | 0.3 | 24.97 | 1700000