## Naini-2
Naini-2 STP, 42 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-04-01 | 43070 | 43.08 | 7.49 | 7.86 | 160 | 22 | 320 | 36 | 294 | 22 | NA | 600 | 0.3 | 23.7 | 1300000
2023-04-02 | 40030 | 40.04 | 7.53 | 7.82 | 155 | 27 | 304 | 32 | 287 | 23 | NA | 800 | 0.2 | 25.6 | 1400000
2023-04-03 | 37960 | 37.96 | 7.18 | 7.31 | 160 | 26 | 316 | 36 | 295 | 25 | NA | 600 | 0.3 | 25.5 | 1700000
2023-04-04 | 38730 | 38.73 | 7.26 | 7.49 | 165 | 21 | 312 | 40 | 285 | 20 | NA | 500 | 0.3 | 25 | 1400000
2023-04-05 | 37470 | 37.47 | 7.38 | 7.76 | 160 | 23 | 328 | 44 | 318 | 22 | NA | 600 | 0.2 | 24.8 | 1300000
2023-04-06 | 37660 | 37.66 | 7.29 | 7.64 | 170 | 25 | 316 | 36 | 298 | 25 | NA | 500 | 0.2 | 25.5 | 1400000
2023-04-07 | 37630 | 37.63 | 7.43 | 7.81 | 160 | 24 | 328 | 40 | 305 | 27 | NA | 700 | 0.2 | 25 | 1300000
2023-04-08 | 36290 | 36.29 | 7.31 | 7.88 | 165 | 26 | 312 | 40 | 296 | 23 | NA | 600 | 0.3 | 23.9 | 1400000
2023-04-09 | 35980 | 35.98 | 7.23 | 7.65 | 160 | 24 | 304 | 36 | 286 | 20 | NA | 500 | 0.2 | 24.3 | 1400000
2023-04-10 | 37060 | 37.07 | 7.19 | 7.41 | 155 | 25 | 308 | 40 | 292 | 20 | NA | 400 | 0.2 | 24.6 | 1300000
2023-04-11 | 36970 | 36.97 | 7.48 | 7.81 | 170 | 26 | 316 | 44 | 302 | 22 | NA | 600 | 0.3 | 25.4 | 1400000
2023-04-12 | 36740 | 36.75 | 7.26 | 7.53 | 165 | 24 | 304 | 44 | 288 | 20 | NA | 500 | 0.2 | 25 | 1700000
2023-04-13 | 34700 | 34.7 | 7.21 | 7.46 | 155 | 22 | 324 | 40 | 297 | 23 | NA | 700 | 0.2 | 24.8 | 1300000
2023-04-14 | 35880 | 35.89 | 7.42 | 7.74 | 170 | 23 | 328 | 36 | 319 | 21 | NA | 500 | 0.3 | 25.2 | 1400000
2023-04-15 | 35370 | 35.37 | 7.33 | 7.66 | 165 | 21 | 316 | 40 | 285 | 20 | NA | 700 | 0.2 | 25.6 | 1700000
2023-04-16 | 35900 | 35.9 | 7.25 | 7.62 | 155 | 20 | 324 | 36 | 307 | 24 | NA | 800 | 0.3 | 24.6 | 1400000
2023-04-17 | 36220 | 36.23 | 7.35 | 7.57 | 160 | 22 | 320 | 44 | 309 | 21 | NA | 600 | 0.2 | 24.3 | 1300000
2023-04-18 | 35950 | 35.96 | 7.25 | 7.68 | 170 | 24 | 312 | 36 | 294 | 20 | NA | 500 | 0.2 | 24.8 | 1400000
2023-04-19 | 35750 | 35.76 | 7.28 | 7.74 | 165 | 24 | 324 | 40 | 304 | 23 | NA | 700 | 0.3 | 26 | 1300000
2023-04-20 | 35770 | 35.78 | 7.22 | 7.56 | 155 | 23 | 316 | 36 | 297 | 24 | NA | 800 | 0.2 | 24.5 | 1400000
2023-04-21 | 34760 | 34.77 | 7.31 | 7.59 | 170 | 25 | 308 | 40 | 288 | 20 | NA | 400 | 0.3 | 25 | 1300000 | Samples were not tested correctly for fecal coliform of effluent and sludge both hence testing was rejected.
2023-04-22 | 35330 | 35.34 | 7.27 | 7.66 | 160 | 22 | 320 | 44 | 295 | 23 | NA | 600 | 0.3 | 24.4 | 1700000
2023-04-23 | 35920 | 35.93 | 7.23 | 7.58 | 155 | 24 | 324 | 40 | 306 | 25 | NA | 700 | 0.2 | 24.7 | 1200000 | Samples were not tested correctly for fecal coliform of effluent and sludge both hence testing was rejected.
2023-04-24 | 33630 | 33.63 | 7.34 | 7.73 | 165 | 23 | 328 | 44 | 302 | 22 | NA | 500 | 0.3 | 25.2 | 1400000
2023-04-25 | 33580 | 33.59 | 7.54 | 7.85 | 160 | 20 | 316 | 36 | 287 | 21 | NA | 700 | 0.3 | 25.5 | 1200000
2023-04-26 | 33010 | 33.01 | 7.42 | 7.83 | 170 | 26 | 352 | 48 | 324 | 28 | NA | 800 | 0.2 | 24.8 | 1700000
2023-04-27 | 33120 | 33.12 | 7.56 | 7.86 | 155 | 21 | 320 | 36 | 281 | 20 | NA | 400 | 0.2 | 24.4 | 1300000
2023-04-28 | 35980 | 35.98 | 7.65 | 7.87 | 160 | 22 | 356 | 40 | 337 | 25 | NA | 600 | 0.3 | 24.1 | 1400000
2023-04-29 | 35730 | 35.73 | 7.25 | 7.7 | 165 | 27 | 340 | 44 | 310 | 26 | NA | 500 | 0.3 | 25.2 | 1200000
2023-04-30 | 37230 | 37.23 | 7.23 | 7.57 | 155 | 24 | 332 | 40 | 287 | 23 | NA | 700 | 0.3 | 24.9 | 1700000
Average | 36314 | 36.3183 | 7.338 | 7.6747 | 161.8333 | 23.5333 | 320.9333 | 39.6 | 299.1667 | 22.6 | NA | 603.3333 | 0.25 | 24.8767 | 1410000
1089.55
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 33010 | 33.01 | 7.18 | 7.31 | 155 | 20 | 304 | 32 | 281 | 20 |  | 400 | 0.2 | 23.7 | 1200000
Max | 43070 | 43.08 | 7.65 | 7.88 | 170 | 27 | 356 | 48 | 337 | 28 |  | 800 | 0.3 | 26 | 1700000

## Phaphamau
Phaphamau STP, 14 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-04-01 | 13440 | 13.44 | 7.28 | 7.69 | 160 | 15 | 364 | 32 | 318 | 22 | NA | 400 | 0.3 | 23.5 | 1700000
2023-04-02 | 13950 | 13.98 | 7.35 | 7.71 | 155 | 14 | 372 | 36 | 325 | 24 | NA | 600 | 0.3 | 23.95 | 1300000
2023-04-03 | 13410 | 13.41 | 7.32 | 7.74 | 160 | 18 | 360 | 40 | 328 | 21 | NA | 700 | 0.2 | 23.5 | 1400000
2023-04-04 | 13460 | 13.46 | 7.24 | 7.63 | 165 | 16 | 368 | 36 | 318 | 23 | NA | 500 | 0.3 | 24.56 | 1700000
2023-04-05 | 12700 | 12.7 | 7.34 | 7.75 | 160 | 14 | 356 | 32 | 317 | 21 | NA | 600 | 0.2 | 23.4 | 1300000
2023-04-06 | 12370 | 12.37 | 7.31 | 7.72 | 165 | 16 | 372 | 36 | 325 | 23 | NA | 700 | 0.3 | 23.29 | 1700000
2023-04-07 | 13240 | 13.24 | 7.25 | 7.67 | 155 | 15 | 356 | 32 | 316 | 24 | NA | 400 | 0.2 | 23.15 | 1300000
2023-04-08 | 13140 | 13.14 | 7.28 | 7.65 | 160 | 14 | 360 | 36 | 320 | 25 | NA | 500 | 0.3 | 24.36 | 1400000
2023-04-09 | 14530 | 14.53 | 7.35 | 7.71 | 160 | 16 | 372 | 40 | 325 | 22 | NA | 600 | 0.2 | 23.67 | 1700000
2023-04-10 | 14050 | 14.05 | 7.31 | 7.65 | 160 | 17 | 364 | 36 | 318 | 23 | NA | 500 | 0.3 | 24.97 | 1400000
2023-04-11 | 14010 | 14.01 | 7.33 | 7.72 | 165 | 16 | 372 | 40 | 331 | 25 | NA | 400 | 0.3 | 23.66 | 1700000
2023-04-12 | 16230 | 16.23 | 7.27 | 7.69 | 170 | 17 | 368 | 32 | 324 | 23 | NA | 600 | 0.2 | 24.18 | 1300000
2023-04-13 | 13460 | 13.46 | 7.36 | 7.72 | 165 | 15 | 364 | 36 | 317 | 21 | NA | 500 | 0.3 | 23.93 | 1400000
2023-04-14 | 12230 | 12.26 | 7.33 | 7.75 | 160 | 16 | 356 | 32 | 315 | 24 | NA | 700 | 0.2 | 23.95 | 1700000
2023-04-15 | 14360 | 14.36 | 7.36 | 7.73 | 165 | 18 | 368 | 36 | 319 | 22 | NA | 500 | 0.3 | 24.15 | 1300000
2023-04-16 | 14690 | 14.69 | 7.29 | 7.71 | 175 | 16 | 360 | 32 | 328 | 25 | NA | 600 | 0.2 | 24.64 | 1400000
2023-04-17 | 14100 | 14.1 | 7.34 | 7.65 | 155 | 18 | 364 | 36 | 326 | 24 | NA | 500 | 0.3 | 23.37 | 1300000
2023-04-18 | 13860 | 13.86 | 7.33 | 7.74 | 160 | 17 | 360 | 44 | 315 | 23 | NA | 700 | 0.2 | 25.69 | 1700000
2023-04-19 | 14820 | 14.82 | 7.26 | 7.54 | 165 | 16 | 356 | 40 | 320 | 25 | NA | 600 | 0.2 | 24.25 | 1400000
2023-04-20 | 13210 | 13.21 | 7.51 | 7.63 | 160 | 17 | 364 | 44 | 318 | 26 | NA | 500 | 0.3 | 25 | 1700000
2023-04-21 | 14310 | 14.31 | 7.25 | 7.64 | 165 | 18 | 368 | 44 | 320 | 23 | NA | 600 | 0.2 | 24.37 | 1300000
2023-04-22 | 13460 | 13.46 | 7.31 | 7.7 | 170 | 16 | 356 | 36 | 310 | 26 | NA | 500 | 0.3 | 24.3 | 1400000
2023-04-23 | 13130 | 13.13 | 7.3 | 7.65 | 162 | 15 | 368 | 40 | 315 | 25 | NA | 600 | 0.2 | 24.38 | 1700000
2023-04-24 | 13140 | 13.14 | 7.34 | 7.73 | 155 | 18 | 380 | 44 | 310 | 23 | NA | 400 | 0.3 | 24.27 | 1300000
2023-04-25 | 13180 | 13.18 | 7.32 | 7.71 | 170 | 15 | 364 | 36 | 327 | 24 | NA | 700 | 0.2 | 23.97 | 1700000
2023-04-26 | 13870 | 13.87 | 7.34 | 7.75 | 165 | 16 | 372 | 40 | 325 | 23 | NA | 500 | 0.3 | 24.18 | 1400000
2023-04-27 | 13520 | 13.52 | 7.31 | 7.65 | 166 | 15 | 368 | 36 | 317 | 25 | NA | 700 | 0.2 | 23.18 | 1300000
2023-04-28 | 13540 | 13.54 | 7.34 | 7.73 | 173 | 18 | 364 | 40 | 323 | 28 | NA | 600 | 0.2 | 23.98 | 1700000
2023-04-29 | 13790 | 13.79 | 7.18 | 7.79 | 175 | 15 | 368 | 44 | 316 | 19 | NA | 500 | 0.3 | 24.8 | 1400000
2023-04-30 | 16160 | 16.16 | 7.19 | 7.78 | 165 | 17 | 360 | 36 | 318 | 18 | NA | 700 | 0.2 | 24.9 | 1300000
Average | 13778.6667 | 13.7807 | 7.3097 | 7.6977 | 163.5333 | 16.1333 | 364.8 | 37.4667 | 320.1333 | 23.3333 | NA | 563.3333 | 0.25 | 24.1167 | 1476666.6667
413.42
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 12230 | 12.26 | 7.18 | 7.54 | 155 | 14 | 356 | 32 | 310 | 18 |  | 400 | 0.2 | 23.15 | 1300000
Max | 16230 | 16.23 | 7.51 | 7.79 | 175 | 18 | 380 | 44 | 331 | 28 |  | 700 | 0.3 | 25.69 | 1700000