## Naini-2
Naini-2 STP, 42 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-02-19 | 36720 | 36.72 | 7.27 | 7.4 | 170 | 23 | 348 | 36 | 320 | 18 | NA | 600 | 0.2 | 24.5 | 1300000
2023-02-20 | 35120 | 35.12 | 7.29 | 7.36 | 165 | 26 | 320 | 32 | 282 | 20 | NA | 700 | 0.2 | - | - | Dewatering building was not operated due to road construction work in front of unit
2023-02-21 | 35410 | 35.41 | 7.28 | 7.33 | 155 | 23 | 328 | 48 | 302 | 26 | NA | 500 | 0.3 | 22.59 | 1700000
2023-02-22 | 36740 | 36.74 | 7.33 | 7.37 | 150 | 26 | 356 | 44 | 308 | 23 | NA | 800 | 0.2 | - | - | Dewatering building was not operated due to road construction work in front of unit
2023-02-23 | 36540 | 36.54 | 7.29 | 7.41 | 160 | 24 | 360 | 28 | 324 | 27 | NA | 700 | 0.3 | - | -
2023-02-24 | 36240 | 36.24 | 7.42 | 7.49 | 155 | 28 | 344 | 44 | 316 | 26 | NA | 800 | 0.2 | 23.22 | 1400000
2023-02-25 | 35460 | 35.46 | 7.39 | 7.48 | 170 | 24 | 368 | 40 | 327 | 29 | NA | 600 | 0.3 | 24.92 | 1700000
2023-02-26 | 36210 | 36.21 | 7.44 | 7.45 | 150 | 25 | 336 | 36 | 315 | 26 | NA | 500 | 0.2 | 25.32 | 1300000
2023-02-27 | 36440 | 36.44 | 7.43 | 7.83 | 155 | 23 | 352 | 44 | 357 | 28 | NA | 600 | 0.3 | 25.4 | 1400000
2023-02-28 | 36120 | 36.12 | 7.57 | 7.81 | 150 | 26 | 324 | 40 | 305 | 25 | NA | 800 | 0.3 | 24.8 | 1300000
Average | 36100 | 36.1 | 7.371 | 7.493 | 158 | 24.8 | 343.6 | 39.2 | 315.6 | 24.8 | NA | 660 | 0.25 | 24.3929 | 1442857.1429
361
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 35120 | 35.12 | 7.27 | 7.33 | 150 | 23 | 320 | 28 | 282 | 18 |  | 500 | 0.2 | 22.59 | 1300000
Max | 36740 | 36.74 | 7.57 | 7.83 | 170 | 28 | 368 | 48 | 357 | 29 |  | 800 | 0.3 | 25.4 | 1700000