## Naini-2
Naini-2 STP, 42 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-06-01 | 36110 | 36.11 | 7.42 | 7.81 | 170 | 22 | 300 | 44 | 287 | 24 | NA | 600 | 0.3 | 25 | 1200000
2023-06-02 | 35570 | 35.57 | 7.49 | 7.87 | 165 | 25 | 312 | 48 | 292 | 27 | NA | 500 | 0.2 | 25.2 | 1400000
2023-06-03 | 34990 | 34.99 | 7.39 | 7.82 | 155 | 20 | 296 | 36 | 284 | 22 | NA | 400 | 0.2 | 25.5 | 1700000
2023-06-04 | 36300 | 36.3 | 7.44 | 7.49 | 160 | 25 | 336 | 40 | 305 | 26 | NA | 700 | 0.3 | 24.9 | 1400000
2023-06-05 | 38420 | 38.42 | 7.35 | 7.74 | 165 | 16 | 292 | 48 | 272 | 21 | NA | 500 | 0.2 | 25.6 | 1200000
2023-06-06 | 38250 | 38.25 | 7.36 | 7.7 | 160 | 20 | 300 | 40 | 278 | 18 | NA | 600 | 0.3 | 25.8 | 1700000
2023-06-07 | 36360 | 36.36 | 7.42 | 7.76 | 170 | 18 | 304 | 48 | 276 | 17 | NA | 400 | 0.3 | 24.3 | 1400000
2023-06-08 | 36540 | 36.54 | 7.35 | 7.67 | 165 | 19 | 312 | 36 | 272 | 20 | NA | 700 | 0.3 | 25.7 | 1200000
2023-06-09 | 37150 | 37.15 | 7.26 | 7.38 | 155 | 22 | 328 | 40 | 280 | 22 | NA | 600 | 0.3 | 26.1 | 1400000
2023-06-10 | 35040 | 35.04 | 7.24 | 7.48 | 175 | 24 | 340 | 48 | 302 | 25 | NA | 500 | 0.2 | 25.4 | 1700000
2023-06-11 | 36830 | 36.83 | 7.35 | 7.59 | 170 | 22 | 348 | 36 | 320 | 23 | NA | 400 | 0.3 | 24.8 | 1400000
2023-06-12 | 36050 | 36.05 | 7.18 | 7.27 | 165 | 25 | 316 | 44 | 284 | 28 | NA | 600 | 0.2 | 26.1 | 1700000
2023-06-13 | 35410 | 35.41 | 7.57 | 7.72 | 175 | 28 | 320 | 48 | 302 | 30 | NA | 500 | 0.3 | 25.9 | 1200000
2023-06-14 | 34550 | 34.55 | 7.22 | 7.38 | 160 | 21 | 328 | 44 | 270 | 25 | NA | 400 | 0.3 | 24.7 | 1100000
2023-06-15 | 35120 | 35.12 | 7.24 | 7.42 | 155 | 22 | 312 | 48 | 272 | 26 | NA | 700 | 0.2 | 24.1 | 1400000
2023-06-16 | 33520 | 33.52 | 7.35 | 7.65 | 160 | 21 | 320 | 40 | 275 | 19 | NA | 500 | 0.3 | 23.2 | 1700000
2023-06-17 | 12020 | 12.02 | 7.14 | 7.37 | 165 | 23 | 304 | 44 | 268 | 18 | NA | 600 | 0.3 | 24.3 | 1100000
2023-06-18 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | - | Plant was shutdown 17.06.2023 at 08:30 AM due to maintenance work in effluent line. Plant was taken into operation at 9:45 AM on 21.06.2023. Subsequently, Mawaiya SPS and Mahewaghat SPS were also stopped.
2023-06-19 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-06-20 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-06-21 | 26640 | 26.64 | 7.04 | 7.28 | 170 | 20 | 356 | 48 | 311 | 25 | NA | 400 | 0.3 | 24.7 | 1200000
2023-06-22 | 37710 | 37.71 | 7.43 | 7.82 | 160 | 21 | 340 | 48 | 308 | 19 | NA | 500 | 0.3 | 25.3 | 1400000
2023-06-23 | 36480 | 36.48 | 7.68 | 7.94 | 165 | 15 | 332 | 44 | 302 | 16 | NA | 400 | 0.2 | 24.9 | 1700000
2023-06-24 | 40770 | 40.77 | 7.65 | 7.98 | 155 | 21 | 304 | 40 | 284 | 24 | NA | 700 | 0.3 | 25.6 | 1200000
2023-06-25 | 38840 | 38.84 | 7.51 | 7.82 | 160 | 14 | 312 | 40 | 279 | 18 | NA | 600 | 0.2 | 25.3 | 1300000
2023-06-26 | 37750 | 37.75 | 7.7 | 7.92 | 165 | 15 | 328 | 44 | 307 | 20 | NA | 500 | 0.3 | 23.9 | 1200000
2023-06-27 | 38630 | 38.63 | 7.51 | 7.86 | 160 | 22 | 320 | 48 | 302 | 21 | NA | 700 | 0.3 | 25.9 | 1700000
2023-06-28 | 39540 | 39.54 | 7.55 | 7.94 | 155 | 18 | 316 | 40 | 296 | 20 | NA | 500 | 0.2 | 24.5 | 1300000
2023-06-29 | 41340 | 41.34 | 7.4 | 7.9 | 160 | 16 | 312 | 44 | 292 | 22 | NA | 600 | 0.2 | 25.8 | 1400000
2023-06-30 | 55890 | 55.89 | 7.21 | 7.8 | 155 | 21 | 352 | 48 | 264 | 25 | NA | 700 | 0.3 | 24.1 | 1200000
Average | 32727.3333 | 32.7273 | 7.387 | 7.6807 | 162.7778 | 20.5926 | 320 | 43.5556 | 288.2963 | 22.2593 | NA | 548.1481 | 0.26296 | 25.0593 | 1388888.8889
981.82
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.04 | 7.27 | 155 | 14 | 292 | 36 | 264 | 16 |  | 400 | 0.2 | 23.2 | 1100000
Max | 55890 | 55.89 | 7.7 | 7.98 | 175 | 28 | 356 | 48 | 320 | 30 |  | 700 | 0.3 | 26.1 | 1700000

## Phaphamau
Phaphamau STP, 14 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-06-01 | 13590 | 13.59 | 7.25 | 7.76 | 155 | 20 | 368 | 36 | 321 | 17 | NA | 400 | 0.2 | 24.09 | 1700000
2023-06-02 | 14070 | 14.07 | 7.31 | 7.77 | 165 | 18 | 364 | 32 | 318 | 18 | NA | 500 | 0.3 | 24.73 | 1400000
2023-06-03 | 14570 | 14.57 | 7.24 | 7.76 | 160 | 16 | 372 | 36 | 316 | 17 | NA | 600 | 0.2 | 23.67 | 1700000
2023-06-04 | 13480 | 13.48 | 7.31 | 7.78 | 155 | 18 | 368 | 40 | 318 | 18 | NA | 500 | 0.3 | 24.8 | 1400000
2023-06-05 | 14140 | 14.14 | 7.33 | 7.75 | 160 | 15 | 360 | 32 | 317 | 14 | NA | 600 | 0.2 | 23.92 | 1700000
2023-06-06 | 14380 | 14.38 | 7.36 | 7.78 | 165 | 18 | 356 | 36 | 318 | 18 | NA | 400 | 0.3 | 23.39 | 1300000
2023-06-07 | 14580 | 14.58 | 7.32 | 7.75 | 160 | 16 | 360 | 40 | 321 | 16 | NA | 500 | 0.2 | 23.73 | 1400000
2023-06-08 | 15270 | 15.27 | 7.34 | 7.78 | 165 | 14 | 364 | 32 | 323 | 15 | NA | 600 | 0.3 | 23.22 | 1700000
2023-06-09 | 14420 | 14.42 | 7.32 | 7.76 | 160 | 16 | 368 | 40 | 315 | 17 | NA | 400 | 0.2 | 24.19 | 1300000
2023-06-10 | 14530 | 14.53 | 7.34 | 7.78 | 170 | 13 | 360 | 32 | 325 | 20 | NA | 700 | 0.3 | 24.73 | 1400000
2023-06-11 | 15060 | 15.06 | 7.35 | 7.76 | 165 | 16 | 368 | 36 | 315 | 22 | NA | 600 | 0.2 | 23.52 | 1700000
2023-06-12 | 15650 | 15.65 | 7.37 | 7.78 | 160 | 15 | 364 | 32 | 317 | 14 | NA | 400 | 0.2 | 23.84 | 1300000
2023-06-13 | 14340 | 14.34 | 7.35 | 7.8 | 170 | 14 | 368 | 36 | 322 | 13 | NA | 600 | 0.2 | 24.16 | 1700000
2023-06-14 | 12650 | 12.65 | 7.36 | 7.79 | 160 | 15 | 360 | 32 | 325 | 15 | NA | 500 | 0.3 | 23.47 | 1400000
2023-06-15 | 13890 | 13.89 | 7.36 | 7.85 | 165 | 14 | 368 | 40 | 316 | 16 | NA | 400 | 0.2 | 24.71 | 1300000
2023-06-16 | 14590 | 14.59 | 7.34 | 7.83 | 160 | 16 | 364 | 36 | 318 | 15 | NA | 600 | 0.3 | 23.22 | 1700000
2023-06-17 | 13820 | 13.82 | 7.36 | 7.86 | 170 | 15 | 360 | 40 | 316 | 12 | NA | 500 | 0.2 | 24.19 | 1400000
2023-06-18 | 15010 | 15.01 | 7.37 | 7.9 | 165 | 18 | 368 | 32 | 317 | 14 | NA | 400 | 0.3 | 23.94 | 1300000
2023-06-19 | 14180 | 14.18 | 7.41 | 7.92 | 160 | 16 | 364 | 36 | 312 | 12 | NA | 600 | 0.2 | 24.1 | 1700000
2023-06-20 | 15410 | 15.41 | 7.4 | 7.83 | 170 | 18 | 360 | 32 | 315 | 15 | NA | 500 | 0.3 | 24.13 | 1400000
2023-06-21 | 14310 | 14.31 | 7.42 | 7.94 | 165 | 16 | 368 | 36 | 314 | 12 | NA | 400 | 0.2 | 23.84 | 1700000
2023-06-22 | 14660 | 14.66 | 7.4 | 7.95 | 160 | 15 | 364 | 40 | 318 | 16 | NA | 600 | 0.3 | 24.28 | 1400000
2023-06-23 | 15610 | 15.61 | 7.35 | 7.85 | 170 | 14 | 360 | 32 | 316 | 15 | NA | 700 | 0.2 | 23.14 | 1700000
2023-06-24 | 14870 | 14.87 | 7.4 | 7.89 | 165 | 16 | 368 | 40 | 312 | 12 | NA | 400 | 0.3 | 24.2 | 1300000
2023-06-25 | 15880 | 15.88 | 7.42 | 7.85 | 160 | 15 | 372 | 44 | 315 | 15 | NA | 600 | 0.2 | 23.15 | 1400000
2023-06-26 | 15440 | 15.44 | 7.43 | 7.88 | 165 | 14 | 360 | 36 | 310 | 13 | NA | 400 | 0.3 | 23.52 | 1300000
2023-06-27 | 14910 | 14.91 | 7.4 | 7.85 | 160 | 16 | 368 | 32 | 314 | 14 | NA | 700 | 0.2 | 24.8 | 1700000
2023-06-28 | 17470 | 17.47 | 7.38 | 7.91 | 170 | 18 | 360 | 40 | 312 | 12 | NA | 400 | 0.3 | 23.22 | 1300000
2023-06-29 | 18110 | 18.11 | 7.41 | 7.85 | 165 | 20 | 356 | 32 | 310 | 11 | NA | 600 | 0.2 | 23.1 | 1700000
2023-06-30 | 19150 | 19.15 | 7.43 | 7.9 | 155 | 17 | 360 | 36 | 313 | 14 | NA | 700 | 0.3 | 23.13 | 1400000
Average | 14934.6667 | 14.9347 | 7.361 | 7.8287 | 163.1667 | 16.0667 | 364 | 35.8667 | 316.6333 | 15.0667 | NA | 526.6667 | 0.24667 | 23.871 | 1493333.3333
448.04
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 12650 | 12.65 | 7.24 | 7.75 | 155 | 13 | 356 | 32 | 310 | 11 |  | 400 | 0.2 | 23.1 | 1300000
Max | 19150 | 19.15 | 7.43 | 7.95 | 170 | 20 | 372 | 44 | 325 | 22 |  | 700 | 0.3 | 24.8 | 1700000