## Naini-2
Naini-2 STP, 42 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 42 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-06-01 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | - | From 01.06.2024 to 06.06.2024: Plant was under shutdown for Reparing work at CCT, Installation of submersible pump in sludge sump and rectification of leakage in header line of MPS. Plant was started at 7 AM on 07.06.2024.
2024-06-02 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2024-06-03 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2024-06-04 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2024-06-05 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2024-06-06 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2024-06-07 | 30880 | 30.88 | 7.93 | 7.99 | 160 | 22 | 344 | 40 | 299 | 25 | NA | 400 | 0.2 | - | - | From 07.06.2024 to 09.06.2024: Due to installation of submersible pumps in sludge sump, sludge withdrawal is zero. Therefore, testing of sludge parameters was not performed on these days.
2024-06-08 | 37700 | 37.7 | 7.98 | 7.97 | 165 | 21 | 360 | 40 | 279 | 28 | NA | 600 | 0.3 | - | -
2024-06-09 | 38190 | 38.19 | 7.72 | 7.91 | 155 | 22 | 368 | 36 | 288 | 26 | NA | 500 | 0.3 | - | -
2024-06-10 | 37460 | 37.46 | 7.64 | 7.88 | 165 | 20 | 360 | 40 | 297 | 25 | NA | 800 | 0.2 | 24.5 | 1700000
2024-06-11 | 37200 | 37.2 | 7.5 | 7.86 | 170 | 21 | 364 | 44 | 285 | 24 | NA | 700 | 0.3 | 23.77 | 1100000
2024-06-12 | 36890 | 36.89 | 7.44 | 7.85 | 180 | 23 | 380 | 40 | 291 | 25 | NA | 400 | 0.3 | 24.81 | 1400000
2024-06-13 | 39320 | 39.32 | 7.35 | 7.96 | 170 | 22 | 360 | 40 | 287 | 22 | NA | 700 | 0.3 | 23.06 | 1100000
2024-06-14 | 36970 | 36.97 | 7.31 | 7.84 | 160 | 23 | 324 | 44 | 280 | 24 | NA | 500 | 0.2 | 23.17 | 1700000
2024-06-15 | 38070 | 38.07 | 7.28 | 7.82 | 155 | 24 | 328 | 48 | 298 | 25 | NA | 600 | 0.3 | 24.11 | 1300000
2024-06-16 | 37120 | 37.12 | 7.23 | 7.9 | 160 | 25 | 320 | 48 | 290 | 24 | NA | 400 | 0.3 | 23.74 | 1100000
2024-06-17 | 38890 | 38.89 | 7.25 | 7.92 | 155 | 24 | 340 | 44 | 288 | 25 | NA | 600 | 0.2 | 24.16 | 1200000
2024-06-18 | 37460 | 37.46 | 7.21 | 7.94 | 165 | 22 | 348 | 40 | 291 | 26 | NA | 400 | 0.2 | 23.88 | 1700000
2024-06-19 | 38900 | 38.9 | 7.28 | 7.95 | 170 | 21 | 352 | 44 | 289 | 28 | NA | 500 | 0.3 | 24.13 | 1300000
2024-06-20 | 42700 | 42.7 | 7.22 | 7.97 | 185 | 22 | 376 | 40 | 300 | 30 | NA | 600 | 0.3 | 23.41 | 1400000
2024-06-21 | 40780 | 40.78 | 7.2 | 7.96 | 175 | 21 | 348 | 36 | 294 | 28 | NA | 400 | 0.2 | 24.11 | 1100000
2024-06-22 | 44610 | 44.61 | 7.18 | 7.9 | 180 | 22 | 360 | 40 | 302 | 36 | NA | 700 | 0.3 | 23.88 | 1300000
2024-06-23 | 41380 | 41.38 | 7.19 | 7.92 | 185 | 24 | 392 | 44 | 304 | 31 | NA | 500 | 0.3 | 24.35 | 1700000
2024-06-24 | 41430 | 41.43 | 7.21 | 7.95 | 175 | 22 | 368 | 40 | 291 | 30 | NA | 600 | 0.2 | 23.91 | 1400000
2024-06-25 | 41430 | 41.43 | 7.28 | 7.92 | 170 | 21 | 352 | 40 | 283 | 28 | NA | 400 | 0.3 | 23.56 | 1300000
2024-06-26 | 45750 | 45.75 | 7.28 | 7.89 | 165 | 22 | 356 | 40 | 288 | 33 | NA | 700 | 0.3 | 24.15 | 1100000
2024-06-27 | 41620 | 41.62 | 7.3 | 7.88 | 175 | 21 | 372 | 36 | 286 | 32 | NA | 500 | 0.2 | 23.97 | 1300000
2024-06-28 | 44800 | 44.8 | 7.31 | 7.9 | 170 | 20 | 360 | 40 | 309 | 35 | NA | 600 | 0.3 | 24.05 | 1200000
2024-06-29 | 40900 | 40.9 | 7.28 | 7.92 | 175 | 21 | 376 | 36 | 301 | 36 | NA | 700 | 0.3 | 23.85 | 1700000
2024-06-30 | 51490 | 51.49 | 7.3 | 7.94 | 180 | 20 | 380 | 36 | 309 | 42 | NA | 800 | 0.3 | 24.1 | 1400000
Average | 32064.6667 | 32.0647 | 7.3696 | 7.9142 | 169.375 | 21.9167 | 357.8333 | 40.6667 | 292.875 | 28.6667 |  | 566.6667 | 0.26667 | 23.9367 | 1357142.8571
961.94
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.18 | 7.82 | 155 | 20 | 320 | 36 | 279 | 22 |  | 400 | 0.2 | 23.06 | 1100000
Max | 51490 | 51.49 | 7.98 | 7.99 | 185 | 25 | 392 | 48 | 309 | 42 |  | 800 | 0.3 | 24.81 | 1700000

## Phaphamau
Phaphamau STP, 14 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 14 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-06-01 | 16720 | 16.72 | 7.49 | 7.91 | 170 | 20 | 308 | 44 | 306 | 28 | NA | 400 | 0.3 | 24.16 | 1300000
2024-06-02 | 16800 | 16.8 | 7.56 | 7.92 | 160 | 19 | 320 | 40 | 320 | 25 | NA | 500 | 0.3 | 23.92 | 1400000
2024-06-03 | 16320 | 16.32 | 7.52 | 7.94 | 155 | 20 | 316 | 44 | 333 | 23 | NA | 400 | 0.3 | 23.12 | 1300000
2024-06-04 | 16450 | 16.45 | 7.6 | 7.93 | 160 | 20 | 308 | 40 | 332 | 20 | NA | 500 | 0.3 | 24.12 | 1300000
2024-06-05 | 16520 | 16.52 | 7.53 | 7.91 | 165 | 19 | 308 | 44 | 303 | 19 | NA | 400 | 0.3 | 23.92 | 1400000
2024-06-06 | 15650 | 15.65 | 7.65 | 7.94 | 155 | 21 | 304 | 44 | 300 | 21 | NA | 600 | 0.2 | 23.27 | 1700000
2024-06-07 | 17310 | 17.31 | 7.71 | 7.94 | 165 | 20 | 320 | 40 | 280 | 17 | NA | 400 | 0.3 | 24.32 | 1300000
2024-06-08 | 14830 | 14.83 | 7.72 | 7.92 | 160 | 21 | 312 | 44 | 252 | 19 | NA | 500 | 0.3 | 23.92 | 1400000
2024-06-09 | 16880 | 16.88 | 7.71 | 7.69 | 170 | 22 | 328 | 40 | 271 | 27 | NA | 600 | 0.2 | 22.73 | 1700000
2024-06-10 | 16920 | 16.92 | 7.65 | 7.94 | 155 | 20 | 304 | 44 | 210 | 20 | NA | 500 | 0.3 | 24.32 | 1400000
2024-06-11 | 15860 | 15.86 | 7.65 | 7.96 | 160 | 20 | 316 | 40 | 220 | 20 | NA | 400 | 0.3 | 23.25 | 1300000
2024-06-12 | 17870 | 17.87 | 7.64 | 7.95 | 165 | 20 | 320 | 44 | 290 | 21 | NA | 600 | 0.2 | 24.32 | 1700000
2024-06-13 | 17630 | 17.63 | 7.62 | 7.96 | 170 | 21 | 336 | 40 | 316 | 20 | NA | 500 | 0.2 | 24 | 1400000
2024-06-14 | 17990 | 17.99 | 7.63 | 7.96 | 160 | 20 | 320 | 44 | 300 | 16 | NA | 400 | 0.2 | 23.91 | 1700000
2024-06-15 | 17920 | 17.92 | 7.5 | 7.96 | 165 | 21 | 320 | 40 | 300 | 17 | NA | 600 | 0.2 | 23.91 | 1700000
2024-06-16 | 17490 | 17.49 | 7.54 | 7.97 | 160 | 20 | 328 | 40 | 332 | 16 | NA | 400 | 0.2 | 24.08 | 1300000
2024-06-17 | 18840 | 18.84 | 7.66 | 7.99 | 160 | 21 | 304 | 44 | 340 | 15 | NA | 500 | 0.2 | 23.52 | 1400000
2024-06-18 | 17320 | 17.32 | 7.61 | 7.89 | 180 | 20 | 332 | 44 | 310 | 16 | NA | 400 | 0.2 | 23.23 | 1300000
2024-06-19 | 17650 | 17.65 | 7.41 | 7.9 | 170 | 21 | 320 | 40 | 310 | 17 | NA | 500 | 0.2 | 23.52 | 1300000
2024-06-20 | 17260 | 17.26 | 7.3 | 7.89 | 170 | 19 | 336 | 44 | 330 | 16 | NA | 600 | 0.2 | 24.13 | 1700000
2024-06-21 | 18070 | 18.07 | 7.33 | 7.86 | 175 | 20 | 344 | 40 | 360 | 14 | NA | 500 | 0.2 | 23.62 | 1400000
2024-06-22 | 22610 | 22.61 | 7.32 | 7.79 | 180 | 19 | 400 | 44 | 372 | 24 | NA | 600 | 0.2 | 24.32 | 1700000
2024-06-23 | 17540 | 17.54 | 7.56 | 7.81 | 175 | 20 | 344 | 40 | 430 | 23 | NA | 500 | 0.3 | 24.13 | 1400000
2024-06-24 | 17360 | 17.36 | 7.67 | 7.86 | 165 | 19 | 340 | 40 | 390 | 17 | NA | 400 | 0.3 | 22.32 | 1300000
2024-06-25 | 19860 | 19.86 | 7.72 | 7.87 | 165 | 21 | 316 | 44 | 330 | 18 | NA | 500 | 0.3 | 24.32 | 1400000
2024-06-26 | 24410 | 24.41 | 7.67 | 7.8 | 175 | 20 | 360 | 44 | 310 | 23 | NA | 400 | 0.2 | 23.91 | 1300000
2024-06-27 | 18640 | 18.64 | 7.59 | 7.84 | 175 | 21 | 348 | 40 | 301 | 17 | NA | 600 | 0.3 | 24.21 | 1400000
2024-06-28 | 18240 | 18.24 | 7.37 | 7.85 | 165 | 20 | 324 | 40 | 360 | 15 | NA | 400 | 0.3 | 24.12 | 1300000
2024-06-29 | 14550 | 14.55 | 7.41 | 7.83 | 170 | 20 | 336 | 40 | 310 | 16 | NA | 500 | 0.3 | 23.92 | 1400000
2024-06-30 | 19650 | 19.65 | 7.3 | 7.87 | 175 | 21 | 320 | 44 | 340 | 20 | NA | 400 | 0.3 | 24.13 | 1700000
Average | 17705.3333 | 17.7053 | 7.5547 | 7.895 | 166.5 | 20.2 | 326.4 | 42 | 315.2667 | 19.3333 |  | 483.3333 | 0.25333 | 23.8223 | 1443333.3333
531.16
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 14550 | 14.55 | 7.3 | 7.69 | 155 | 19 | 304 | 40 | 210 | 14 |  | 400 | 0.2 | 22.32 | 1300000
Max | 24410 | 24.41 | 7.72 | 7.99 | 180 | 22 | 400 | 44 | 430 | 28 |  | 600 | 0.3 | 24.32 | 1700000

## Jhunsi
JHUNSI STP, 16 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 16 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-06-01 | 9530 | 9.53 | 7.83 | 7.68 | 180 | 16 | 364 | 44 | 295 | 19 | NA | 500 | 0.3 | 23.18 | 1300000 | From 01.06.2024 to 06.06.2024: 1.Sewage from 9 I&Ds is coming into SPS, howver from 03.06.2024 to 05.06.2024, Sewage from 6 I&Ds on the side of Dham Nalla is bypassed for connecting newly laid trunk sewer in between Dham Nalla & Shastri Bridge SPS with main trunk sewer. 2. Due to work of Road Widening by Irrigation Department as part of Development works for Mahakumbh-2025, I&D structure of Bhola Mandir Nalla, Gangoli Shivalay - 1 nalla are dismantled on 05.04.2024, 19.05.2024 respectively and sewage is not coming to Shastri Bridge SPS. 3. Due to start of replacement work of trunk sewer after I&D of Bhola Mandir Nalla, sewage from Augharwa nalla is not coming to SPS from 08.05.2024. 4. Due to road widening works, joint between manhole and connecting pipeline from I&D of Dham Nalla is broken, hence sewage from Dham nalla is not coming to SPS from 24.05.2024. 5. Due to road widening works, various issues in I&Ds, Trunk Sewer and overflow from one newly constructed manhole, sewage received from tapped I&Ds is less. 6. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2024-06-02 | 9540 | 9.54 | 7.77 | 7.69 | 160 | 14 | 344 | 40 | 290 | 20 | NA | 400 | 0.3 | 24.46 | 1400000
2024-06-03 | 9200 | 9.2 | 7.86 | 7.73 | 165 | 16 | 348 | 44 | 285 | 18 | NA | 600 | 0.3 | 23.48 | 1700000
2024-06-04 | 9230 | 9.23 | 7.8 | 7.76 | 160 | 15 | 340 | 40 | 310 | 17 | NA | 700 | 0.3 | 23.88 | 1100000
2024-06-05 | 9130 | 9.13 | 7.78 | 7.7 | 165 | 16 | 344 | 44 | 289 | 19 | NA | 500 | 0.3 | 24.63 | 1400000
2024-06-06 | 10500 | 10.5 | 7.79 | 7.69 | 155 | 16 | 336 | 40 | 307 | 18 | NA | 400 | 0.2 | 24.18 | 1300000
2024-06-07 | 7600 | 7.6 | 7.84 | 7.7 | 160 | 15 | 340 | 36 | 297 | 17 | NA | 600 | 0.2 | 23.77 | 1200000 | From 07.06.2024 to 12.06.2024: Plant was under shutdown from 7 PM on 07.06.2024 for Reparing of rising main from Shastri Bridge SPS and shifting of Air release valves in this rising main. Plant was started at 12 PM on 12.06.2024.
2024-06-08 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2024-06-09 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2024-06-10 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2024-06-11 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2024-06-12 | 5480 | 5.48 | 7.73 | 7.65 | 160 | 17 | 344 | 32 | 310 | 18 | NA | 500 | 0.2 | 23.45 | 1100000
2024-06-13 | 11420 | 11.42 | 7.85 | 7.77 | 165 | 16 | 336 | 40 | 290 | 19 | NA | 600 | 0.2 | 24.66 | 1400000 | From 13.06.2024 to 26.06.2024: 1.Sewage from 7 I&Ds is coming into SPS. 2. Due to work of Road Widening by Irrigation Department as part of Development works for Mahakumbh-2025, I&D structure of Bhola Mandir Nalla, Gangoli Shivalay - 1 & 2 nalla are dismantled and sewage of Ulta Quila-1 nalla is diverted on 05.04.2024, 19.05.2024, 14.06.2024 & 13.06.2024 respectively and sewage is not coming to Shastri Bridge SPS. 3. Due to start of replacement work of trunk sewer after I&D of Bhola Mandir Nalla, sewage from Augharwa nalla is not coming to SPS from 08.05.2024. 4. Due to road widening works, joint between manhole and connecting pipeline from I&D of Dham Nalla is broken, hence sewage from Dham nalla is not coming to SPS from 24.05.2024. 5. Due to road widening works, various issues in I&Ds, Trunk Sewer, sewage received from tapped I&Ds is less. 6. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2024-06-14 | 11050 | 11.05 | 7.78 | 7.71 | 165 | 17 | 340 | 44 | 287 | 20 | NA | 700 | 0.3 | 24.09 | 1300000
2024-06-15 | 11250 | 11.25 | 7.85 | 7.77 | 185 | 14 | 372 | 36 | 285 | 18 | NA | 400 | 0.3 | 23.73 | 1200000
2024-06-16 | 11750 | 11.75 | 7.78 | 7.8 | 160 | 16 | 344 | 40 | 290 | 17 | NA | 600 | 0.2 | 24.17 | 1700000
2024-06-17 | 11680 | 11.68 | 7.74 | 7.78 | 170 | 15 | 360 | 44 | 276 | 19 | NA | 500 | 0.2 | 23.55 | 1300000
2024-06-18 | 10770 | 10.77 | 7.81 | 7.75 | 160 | 16 | 332 | 40 | 283 | 20 | NA | 700 | 0.2 | 24.12 | 1100000
2024-06-19 | 10150 | 10.15 | 7.76 | 7.88 | 155 | 15 | 336 | 44 | 297 | 19 | NA | 500 | 0.2 | 23.66 | 1200000
2024-06-20 | 12630 | 12.63 | 7.85 | 7.69 | 160 | 14 | 340 | 36 | 290 | 17 | NA | 500 | 0.3 | 24.16 | 1400000
2024-06-21 | 10350 | 10.35 | 7.82 | 7.75 | 170 | 15 | 350 | 40 | 296 | 16 | NA | 700 | 0.3 | 23.56 | 1400000
2024-06-22 | 12680 | 12.68 | 7.82 | 7.73 | 165 | 14 | 344 | 36 | 282 | 18 | NA | 600 | 0.2 | 23.45 | 1700000
2024-06-23 | 11250 | 11.25 | 7.72 | 7.63 | 160 | 15 | 348 | 40 | 293 | 17 | NA | 400 | 0.3 | 24.72 | 1400000
2024-06-24 | 12000 | 12 | 7.81 | 7.77 | 165 | 16 | 340 | 44 | 280 | 19 | NA | 600 | 0.2 | 23.37 | 1200000
2024-06-25 | 11620 | 11.62 | 7.8 | 7.84 | 160 | 15 | 328 | 40 | 276 | 20 | NA | 400 | 0.2 | 24.11 | 1700000
2024-06-26 | 13980 | 13.98 | 7.76 | 7.71 | 165 | 16 | 340 | 44 | 273 | 19 | NA | 500 | 0.2 | 23.45 | 1400000
2024-06-27 | 11320 | 11.32 | 7.8 | 7.75 | 160 | 15 | 332 | 40 | 284 | 18 | NA | 400 | 0.3 | 23.11 | 1700000 | From 27.06.2024 to 30.06.2024: 1.Sewage from 6 I&Ds is coming into SPS. 2. Due to work of Road Widening by Irrigation Department as part of Development works for Mahakumbh-2025, I&D structure of Bhola Mandir Nalla, Gangoli Shivalay - 1 & 2 Nalla, Savitri nalla & Dham Nalla are dismantled and sewage of Ulta Quila-1 nalla is diverted on 05.04.2024, 19.05.2024, 14.06.2024, 27.06.2024 & 13.06.2024 respectively and sewage is not coming to Shastri Bridge SPS. 3. Due to start of replacement work of trunk sewer after I&D of Bhola Mandir Nalla, sewage from Augharwa nalla is not coming to SPS from 08.05.2024. 4. Due to road widening works, joint between manhole and connecting pipeline from I&D of Dham Nalla is broken, hence sewage from Dham nalla is not coming to SPS from 24.05.2024. 5. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2024-06-28 | 11740 | 11.74 | 7.86 | 7.78 | 165 | 16 | 348 | 44 | 274 | 19 | NA | 500 | 0.2 | 22.81 | 1400000
2024-06-29 | 10950 | 10.95 | 7.62 | 7.8 | 170 | 15 | 344 | 40 | 279 | 20 | NA | 600 | 0.2 | 23.44 | 1100000
2024-06-30 | 10500 | 10.5 | 7.88 | 7.79 | 160 | 16 | 328 | 44 | 270 | 18 | NA | 500 | 0.2 | 23.87 | 1200000
Average | 9243.3333 | 9.2433 | 7.7965 | 7.7423 | 164.0385 | 15.4231 | 343.1538 | 40.6154 | 288 | 18.4231 |  | 534.6154 | 0.24231 | 23.81 | 1357692.3077
277.3
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.62 | 7.63 | 155 | 14 | 328 | 32 | 270 | 16 |  | 400 | 0.2 | 22.81 | 1100000
Max | 13980 | 13.98 | 7.88 | 7.88 | 185 | 17 | 372 | 44 | 310 | 20 |  | 700 | 0.3 | 24.72 | 1700000