## Naini-2
Naini-2 STP, 42 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 42 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-03-01 | 37800 | 37.8 | 7.48 | 7.87 | 170 | 20 | 332 | 40 | 278 | 31 | NA | 500 | 0.2 | 25.6 | 1300000
2024-03-02 | 37230 | 37.23 | 7.4 | 7.9 | 180 | 21 | 344 | 36 | 270 | 25 | NA | 400 | 0.3 | 24.2 | 1100000
2024-03-03 | 44360 | 44.36 | 7.36 | 7.87 | 175 | 20 | 368 | 40 | 278 | 30 | NA | 600 | 0.2 | 23.41 | 1400000
2024-03-04 | 37470 | 37.47 | 7.45 | 7.88 | 170 | 20 | 408 | 32 | 249 | 26 | NA | 400 | 0.2 | 23.45 | 1700000
2024-03-05 | 36870 | 36.87 | 7.41 | 7.91 | 165 | 21 | 364 | 40 | 270 | 22 | NA | 500 | 0.3 | 22.81 | 1200000
2024-03-06 | 37570 | 37.57 | 7.4 | 7.93 | 170 | 20 | 348 | 40 | 286 | 19 | NA | 400 | 0.3 | 23.01 | 1300000
2024-03-07 | 35840 | 35.84 | 7.43 | 7.92 | 165 | 21 | 332 | 44 | 290 | 20 | NA | 600 | 0.2 | 24.15 | 1700000
2024-03-08 | 37200 | 37.2 | 7.45 | 7.9 | 175 | 20 | 340 | 40 | 274 | 21 | NA | 400 | 0.3 | 23.8 | 1300000
2024-03-09 | 34660 | 34.66 | 7.53 | 7.91 | 170 | 21 | 324 | 44 | 264 | 20 | NA | 500 | 0.3 | 24.13 | 1100000
2024-03-10 | 35400 | 35.4 | 7.48 | 7.9 | 165 | 20 | 320 | 40 | 273 | 21 | NA | 600 | 0.2 | 23.92 | 1400000
2024-03-11 | 35310 | 35.31 | 7.5 | 7.89 | 175 | 21 | 340 | 44 | 268 | 22 | NA | 700 | 0.3 | 24.08 | 1700000
2024-03-12 | 36460 | 36.46 | 7.52 | 7.8 | 170 | 20 | 324 | 40 | 277 | 20 | NA | 600 | 0.3 | 24.17 | 1700000
2024-03-13 | 37100 | 37.1 | 7.49 | 7.93 | 175 | 22 | 360 | 44 | 283 | 24 | NA | 400 | 0.2 | 24.1 | 1200000
2024-03-14 | 36370 | 36.37 | 7.52 | 7.9 | 170 | 23 | 344 | 44 | 273 | 23 | NA | 500 | 0.2 | 23.81 | 1100000
2024-03-15 | 36670 | 36.67 | 7.5 | 7.89 | 175 | 22 | 328 | 48 | 264 | 20 | NA | 400 | 0.3 | 24.22 | 1400000
2024-03-16 | 36270 | 36.27 | 7.53 | 7.91 | 180 | 23 | 332 | 44 | 273 | 23 | NA | 700 | 0.3 | 24.31 | 1200000
2024-03-17 | 37610 | 37.61 | 7.46 | 7.9 | 175 | 24 | 320 | 48 | 280 | 24 | NA | 600 | 0.2 | 23.97 | 1700000
2024-03-18 | 37870 | 37.87 | 7.45 | 7.94 | 170 | 22 | 328 | 44 | 275 | 25 | NA | 700 | 0.3 | 24.71 | 1100000
2024-03-19 | 37300 | 37.3 | 7.42 | 7.95 | 180 | 20 | 368 | 40 | 279 | 26 | NA | 400 | 0.2 | 24.5 | 1400000
2024-03-20 | 37700 | 37.7 | 7.4 | 7.94 | 170 | 18 | 340 | 40 | 273 | 25 | NA | 600 | 0.3 | 24.35 | 1200000
2024-03-21 | 34440 | 34.44 | 7.39 | 7.96 | 165 | 19 | 332 | 44 | 281 | 24 | NA | 500 | 0.3 | 24.15 | 1400000
2024-03-22 | 38190 | 38.19 | 7.38 | 7.97 | 160 | 20 | 336 | 40 | 290 | 25 | NA | 700 | 0.3 | 23.78 | 1100000
2024-03-23 | 38200 | 38.2 | 7.48 | 7.96 | 155 | 19 | 320 | 44 | 262 | 24 | NA | 600 | 0.2 | 23.91 | 1400000
2024-03-24 | 37660 | 37.66 | 7.7 | 7.98 | 160 | 20 | 312 | 40 | 276 | 23 | NA | 400 | 0.3 | 24.03 | 1300000
2024-03-25 | 41530 | 41.53 | 7.71 | 7.97 | 165 | 19 | 348 | 44 | 269 | 22 | NA | 700 | 0.2 | 23.98 | 1700000
2024-03-26 | 41430 | 41.43 | 7.67 | 7.96 | 160 | 20 | 360 | 40 | 274 | 23 | NA | 500 | 0.3 | 24.1 | 1200000
2024-03-27 | 40100 | 40.1 | 7.6 | 7.95 | 165 | 19 | 340 | 44 | 270 | 22 | NA | 400 | 0.3 | 24.78 | 1700000
2024-03-28 | 37560 | 37.56 | 7.52 | 7.98 | 170 | 20 | 348 | 40 | 282 | 24 | NA | 600 | 0.3 | 23.41 | 1100000
2024-03-29 | 35970 | 35.97 | 7.5 | 7.99 | 165 | 19 | 332 | 40 | 268 | 23 | NA | 700 | 0.3 | 24 | 1400000
2024-03-30 | 37950 | 37.95 | 7.48 | 7.99 | 160 | 18 | 324 | 36 | 277 | 21 | NA | 500 | 0.3 | 24.05 | 1200000
2024-03-31 | 36440 | 36.44 | 7.55 | 8 | 165 | 17 | 320 | 40 | 283 | 22 | NA | 400 | 0.3 | 25.3 | 1700000
Average | 37500.9677 | 37.501 | 7.489 | 7.9274 | 168.871 | 20.2903 | 339.871 | 41.4194 | 274.4839 | 23.2258 |  | 532.2581 | 0.26452 | 24.0706 | 1367741.9355
1162.53
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 34440 | 34.44 | 7.36 | 7.8 | 155 | 17 | 312 | 32 | 249 | 19 |  | 400 | 0.2 | 22.81 | 1100000
Max | 44360 | 44.36 | 7.71 | 8 | 180 | 24 | 408 | 48 | 290 | 31 |  | 700 | 0.3 | 25.6 | 1700000

## Phaphamau
Phaphamau STP, 14 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 14 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-03-01 | 16620 | 16.62 | 7.45 | 7.87 | 160 | 19 | 304 | 40 | 300 | 26 | NA | 600 | 0.2 | 22.5 | 1700000
2024-03-02 | 18870 | 18.87 | 7.45 | 7.88 | 160 | 17 | 308 | 36 | 305 | 23 | NA | 500 | 0.2 | 23.53 | 1400000
2024-03-03 | 20470 | 20.47 | 7.5 | 7.81 | 165 | 17 | 324 | 40 | 340 | 30 | NA | 400 | 0.2 | 22.54 | 1300000
2024-03-04 | 16740 | 16.74 | 7.42 | 7.75 | 170 | 19 | 328 | 36 | 380 | 42 | NA | 500 | 0.3 | 22.14 | 1400000
2024-03-05 | 18150 | 18.15 | 7.55 | 7.82 | 165 | 18 | 304 | 36 | 300 | 30 | NA | 400 | 0.3 | 23.22 | 1300000
2024-03-06 | 19340 | 19.34 | 7.53 | 7.85 | 160 | 16 | 316 | 32 | 265 | 25 | NA | 600 | 0.2 | 23.53 | 1700000
2024-03-07 | 17160 | 17.16 | 7.45 | 7.86 | 165 | 17 | 328 | 36 | 252 | 23 | NA | 600 | 0.2 | 22.81 | 1700000
2024-03-08 | 18630 | 18.63 | 7.4 | 7.83 | 160 | 18 | 324 | 36 | 270 | 24 | NA | 500 | 0.3 | 23.49 | 1400000
2024-03-09 | 17760 | 17.76 | 7.46 | 7.84 | 160 | 17 | 336 | 36 | 275 | 23 | NA | 600 | 0.2 | 23.29 | 1700000
2024-03-10 | 19240 | 19.24 | 7.44 | 7.83 | 165 | 17 | 332 | 36 | 271 | 24 | NA | 400 | 0.3 | 24.03 | 1400000
2024-03-11 | 18610 | 18.61 | 7.45 | 7.86 | 160 | 18 | 312 | 36 | 250 | 22 | NA | 500 | 0.3 | 23.02 | 1700000
2024-03-12 | 18770 | 18.77 | 7.43 | 7.85 | 155 | 17 | 304 | 36 | 245 | 23 | NA | 600 | 0.2 | 22.63 | 1400000
2024-03-13 | 17020 | 17.02 | 7.5 | 7.83 | 160 | 18 | 308 | 40 | 260 | 23 | NA | 400 | 0.2 | 23.55 | 1700000
2024-03-14 | 19240 | 19.24 | 7.54 | 7.83 | 165 | 19 | 304 | 36 | 242 | 24 | NA | 600 | 0.2 | 24.2 | 1700000
2024-03-15 | 19690 | 19.69 | 7.51 | 7.86 | 160 | 18 | 320 | 40 | 245 | 22 | NA | 500 | 0.2 | 23.29 | 1400000
2024-03-16 | 15880 | 15.88 | 7.5 | 7.87 | 165 | 18 | 328 | 40 | 270 | 21 | NA | 400 | 0.3 | 23.55 | 1300000
2024-03-17 | 15850 | 15.85 | 7.6 | 7.9 | 170 | 19 | 336 | 36 | 270 | 25 | NA | 400 | 0.3 | 23.22 | 1300000
2024-03-18 | 19920 | 19.92 | 7.62 | 7.8 | 165 | 20 | 340 | 40 | 272 | 26 | NA | 600 | 0.2 | 23.45 | 1700000
2024-03-19 | 22100 | 22.1 | 7.55 | 7.7 | 160 | 20 | 316 | 40 | 275 | 16 | NA | 400 | 0.3 | 23.29 | 1300000
2024-03-20 | 18640 | 18.64 | 7.49 | 7.66 | 165 | 19 | 312 | 36 | 240 | 21 | NA | 500 | 0.3 | 22.23 | 1400000
2024-03-21 | 15460 | 15.46 | 7.42 | 7.63 | 160 | 18 | 336 | 40 | 251 | 22 | NA | 600 | 0.2 | 24.2 | 1700000
2024-03-22 | 17270 | 17.27 | 7.46 | 7.67 | 165 | 19 | 320 | 40 | 260 | 23 | NA | 500 | 0.2 | 23.09 | 1400000
2024-03-23 | 17730 | 17.73 | 7.45 | 7.7 | 165 | 18 | 324 | 36 | 275 | 20 | NA | 400 | 0.3 | 23.58 | 1300000
2024-03-24 | 18280 | 18.28 | 7.53 | 7.68 | 165 | 19 | 328 | 36 | 253 | 17 | NA | 600 | 0.2 | 23.45 | 1700000
2024-03-25 | 18530 | 18.53 | 7.55 | 7.65 | 160 | 20 | 316 | 40 | 232 | 19 | NA | 400 | 0.3 | 23.23 | 1300000
2024-03-26 | 20040 | 20.04 | 7.6 | 7.66 | 155 | 18 | 308 | 36 | 222 | 15 | NA | 400 | 0.3 | 24.29 | 1700000
2024-03-27 | 15750 | 15.75 | 7.52 | 7.7 | 160 | 19 | 316 | 40 | 251 | 18 | NA | 600 | 0.2 | 21.23 | 1700000
2024-03-28 | 15160 | 15.16 | 7.56 | 7.72 | 165 | 20 | 320 | 40 | 270 | 17 | NA | 500 | 0.3 | 24.29 | 1400000
2024-03-29 | 15500 | 15.5 | 7.56 | 7.75 | 175 | 20 | 332 | 40 | 280 | 21 | NA | 400 | 0.3 | 24.29 | 1400000
2024-03-30 | 15420 | 15.42 | 7.52 | 7.71 | 180 | 21 | 344 | 44 | 290 | 24 | NA | 600 | 0.2 | 23.29 | 1700000
2024-03-31 | 15980 | 15.98 | 7.59 | 7.74 | 175 | 19 | 348 | 40 | 300 | 22 | NA | 400 | 0.3 | 23.22 | 1300000
Average | 17865.1613 | 17.8652 | 7.5032 | 7.7777 | 163.871 | 18.4516 | 321.8065 | 37.9355 | 271.3226 | 22.9355 |  | 496.7742 | 0.24839 | 23.2797 | 1500000
553.82
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 15160 | 15.16 | 7.4 | 7.63 | 155 | 16 | 304 | 32 | 222 | 15 |  | 400 | 0.2 | 21.23 | 1300000
Max | 22100 | 22.1 | 7.62 | 7.9 | 180 | 21 | 348 | 44 | 380 | 42 |  | 600 | 0.3 | 24.29 | 1700000

## Jhunsi
JHUNSI STP, 16 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 16 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2024-03-01 | 13180 | 13.18 | 7.77 | 7.63 | 160 | 14 | 336 | 40 | 290 | 19 | NA | 400 | 0.3 | 24.16 | 1200000 | From 01.03.2024 to 31.03.2024: 1. Sewage from 13 I&Ds is coming into SPS. 2. Due to various issues in I&Ds, Trunk Sewer and overflow at I&D of Bhola Mandir Nalla & one newly constructed manhole, sewage received from tapped I&Ds is less. 3. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2024-03-02 | 12750 | 12.75 | 7.68 | 7.59 | 155 | 16 | 324 | 44 | 281 | 18 | NA | 600 | 0.2 | 23.78 | 1300000
2024-03-03 | 17040 | 17.04 | 7.65 | 7.55 | 160 | 15 | 340 | 36 | 296 | 17 | NA | 500 | 0.2 | 24.27 | 1100000
2024-03-04 | 13010 | 13.01 | 7.5 | 7.42 | 165 | 14 | 336 | 40 | 287 | 19 | NA | 400 | 0.3 | 23.57 | 1400000
2024-03-05 | 12970 | 12.97 | 7.56 | 7.45 | 155 | 14 | 344 | 36 | 290 | 17 | NA | 600 | 0.3 | 24.12 | 1700000
2024-03-06 | 11070 | 11.07 | 7.83 | 7.68 | 165 | 15 | 340 | 44 | 310 | 18 | NA | 400 | 0.3 | 24.55 | 1300000
2024-03-07 | 12740 | 12.74 | 7.78 | 7.65 | 175 | 15 | 348 | 40 | 308 | 19 | NA | 500 | 0.2 | 23.64 | 1200000
2024-03-08 | 13320 | 13.32 | 7.72 | 7.59 | 160 | 14 | 336 | 40 | 314 | 20 | NA | 600 | 0.3 | 23.37 | 1400000
2024-03-09 | 12300 | 12.3 | 7.74 | 7.58 | 155 | 15 | 340 | 36 | 290 | 17 | NA | 500 | 0.2 | 24.17 | 1300000
2024-03-10 | 13230 | 13.23 | 7.6 | 7.57 | 160 | 14 | 324 | 40 | 281 | 20 | NA | 600 | 0.3 | 23.85 | 1700000
2024-03-11 | 12190 | 12.19 | 7.66 | 7.57 | 155 | 16 | 320 | 44 | 277 | 19 | NA | 500 | 0.2 | 23.44 | 1300000
2024-03-12 | 12660 | 12.66 | 7.71 | 7.64 | 165 | 16 | 336 | 40 | 320 | 17 | NA | 400 | 0.3 | 24.03 | 1400000
2024-03-13 | 11780 | 11.78 | 7.27 | 7.4 | 155 | 15 | 328 | 36 | 315 | 18 | NA | 600 | 0.3 | 24.38 | 1300000
2024-03-14 | 11090 | 11.09 | 7.83 | 7.63 | 160 | 14 | 340 | 36 | 285 | 19 | NA | 500 | 0.3 | 23.15 | 1100000
2024-03-15 | 11410 | 11.41 | 7.79 | 7.66 | 165 | 15 | 336 | 40 | 307 | 17 | NA | 600 | 0.2 | 23.77 | 1200000
2024-03-16 | 11300 | 11.3 | 7.77 | 7.67 | 160 | 16 | 328 | 44 | 290 | 18 | NA | 400 | 0.2 | 24.16 | 1400000
2024-03-17 | 11640 | 11.64 | 7.74 | 7.63 | 155 | 14 | 340 | 40 | 307 | 20 | NA | 600 | 0.3 | 23.54 | 1300000
2024-03-18 | 11020 | 11.02 | 7.85 | 7.65 | 165 | 15 | 336 | 36 | 310 | 17 | NA | 700 | 0.3 | 23.15 | 1400000
2024-03-19 | 12320 | 12.32 | 7.88 | 7.67 | 160 | 14 | 328 | 44 | 296 | 19 | NA | 500 | 0.3 | 23.67 | 1100000
2024-03-20 | 11810 | 11.81 | 7.84 | 7.66 | 165 | 15 | 332 | 36 | 288 | 18 | NA | 400 | 0.2 | 22.96 | 1300000
2024-03-21 | 11260 | 11.26 | 7.77 | 7.56 | 155 | 14 | 340 | 40 | 278 | 17 | NA | 600 | 0.3 | 24.16 | 1700000
2024-03-22 | 11410 | 11.41 | 7.79 | 7.61 | 160 | 13 | 328 | 36 | 308 | 20 | NA | 500 | 0.2 | 23.58 | 1400000
2024-03-23 | 10520 | 10.52 | 7.74 | 7.58 | 165 | 15 | 312 | 40 | 291 | 18 | NA | 400 | 0.3 | 24.14 | 1200000
2024-03-24 | 11120 | 11.12 | 7.7 | 7.6 | 155 | 13 | 320 | 36 | 280 | 19 | NA | 600 | 0.2 | 24.12 | 1700000
2024-03-25 | 12170 | 12.17 | 7.69 | 7.62 | 160 | 15 | 324 | 40 | 278 | 18 | NA | 500 | 0.2 | 23.87 | 1300000
2024-03-26 | 11700 | 11.7 | 7.79 | 7.66 | 155 | 14 | 328 | 36 | 297 | 17 | NA | 400 | 0.3 | 24.19 | 1200000
2024-03-27 | 11040 | 11.04 | 7.71 | 7.65 | 165 | 15 | 336 | 40 | 290 | 19 | NA | 600 | 0.3 | 23.67 | 1400000
2024-03-28 | 11060 | 11.06 | 7.56 | 7.48 | 160 | 14 | 340 | 32 | 304 | 17 | NA | 500 | 0.2 | 24.23 | 1300000
2024-03-29 | 10760 | 10.76 | 7.73 | 7.69 | 155 | 15 | 328 | 36 | 293 | 20 | NA | 400 | 0.3 | 23.17 | 1400000
2024-03-30 | 10740 | 10.74 | 7.77 | 7.65 | 165 | 14 | 336 | 40 | 287 | 17 | NA | 600 | 0.2 | 24.08 | 1300000
2024-03-31 | 10920 | 10.92 | 7.69 | 7.52 | 160 | 17 | 340 | 44 | 283 | 20 | NA | 500 | 0.2 | 24.18 | 1100000
Average | 11984.8387 | 11.9848 | 7.7132 | 7.5971 | 160.3226 | 14.6774 | 333.0323 | 39.0968 | 294.5484 | 18.3226 |  | 512.9032 | 0.25484 | 23.8426 | 1335483.871
371.53
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 10520 | 10.52 | 7.27 | 7.4 | 155 | 13 | 312 | 32 | 277 | 17 |  | 400 | 0.2 | 22.96 | 1100000
Max | 17040 | 17.04 | 7.88 | 7.69 | 175 | 17 | 348 | 44 | 320 | 20 |  | 700 | 0.3 | 24.55 | 1700000