## Naini-2
Naini-2 STP, 42 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 42 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-11-01 | 38540 | 38.54 | 7.72 | 7.86 | 160 | 21 | 310 | 42 | 260 | 24 | NA | 600 | 0.2 | 24.84 | 1200000
2023-11-02 | 36010 | 36.01 | 7.74 | 7.89 | 155 | 20 | 322 | 41 | 275 | 21 | NA | 500 | 0.2 | 25.11 | 1700000
2023-11-03 | 37140 | 37.14 | 7.7 | 7.91 | 165 | 21 | 330 | 44 | 282 | 20 | NA | 400 | 0.3 | 24.68 | 1200000
2023-11-04 | 37400 | 37.4 | 7.68 | 7.87 | 160 | 23 | 320 | 48 | 273 | 22 | NA | 600 | 0.2 | 25.2 | 1400000
2023-11-05 | 39280 | 39.28 | 7.77 | 7.89 | 155 | 22 | 325 | 46 | 278 | 21 | NA | 700 | 0.3 | 23.87 | 1100000
2023-11-06 | 36850 | 36.85 | 7.78 | 7.87 | 160 | 24 | 340 | 45 | 284 | 23 | NA | 600 | 0.2 | 24.21 | 1300000
2023-11-07 | 37500 | 37.5 | 7.72 | 7.88 | 165 | 22 | 334 | 46 | 280 | 20 | NA | 400 | 0.3 | 24.4 | 1400000
2023-11-08 | 38890 | 38.89 | 7.74 | 7.86 | 155 | 21 | 320 | 44 | 267 | 23 | NA | 500 | 0.2 | 25.14 | 1200000
2023-11-09 | 39160 | 39.16 | 7.82 | 7.92 | 160 | 20 | 344 | 40 | 282 | 21 | NA | 400 | 0.3 | 24.37 | 1700000
2023-11-10 | 39170 | 39.17 | 7.74 | 7.89 | 165 | 22 | 332 | 42 | 276 | 20 | NA | 600 | 0.2 | 23.86 | 1300000
2023-11-11 | 40220 | 40.22 | 7.71 | 7.86 | 170 | 21 | 340 | 44 | 283 | 24 | NA | 700 | 0.2 | 24.06 | 1100000
2023-11-12 | 40540 | 40.54 | 7.69 | 7.88 | 175 | 22 | 368 | 43 | 288 | 23 | NA | 500 | 0.2 | 24.14 | 1400000
2023-11-13 | 39550 | 39.55 | 7.67 | 7.85 | 175 | 20 | 350 | 46 | 291 | 25 | NA | 700 | 0.3 | 23.91 | 1200000
2023-11-14 | 38080 | 38.08 | 7.68 | 7.87 | 160 | 18 | 328 | 44 | 293 | 24 | NA | 600 | 0.2 | 24.35 | 1700000
2023-11-15 | 37200 | 37.2 | 7.66 | 7.84 | 165 | 19 | 318 | 45 | 275 | 26 | NA | 700 | 0.2 | 23.81 | 1400000
2023-11-16 | 37630 | 37.63 | 7.64 | 7.85 | 155 | 20 | 322 | 44 | 278 | 25 | NA | 500 | 0.3 | 24.3 | 1300000
2023-11-17 | 38420 | 38.42 | 7.62 | 7.84 | 160 | 19 | 344 | 40 | 283 | 20 | NA | 600 | 0.3 | 25.07 | 1200000
2023-11-18 | 37660 | 37.66 | 7.7 | 7.9 | 175 | 18 | 350 | 38 | 288 | 17 | NA | 400 | 0.2 | 24.61 | 1300000
2023-11-19 | 39340 | 39.34 | 7.79 | 7.89 | 170 | 19 | 352 | 44 | 280 | 16 | NA | 700 | 0.3 | 24.1 | 1400000
2023-11-20 | 39300 | 39.3 | 7.8 | 7.91 | 175 | 23 | 364 | 48 | 271 | 16 | NA | 500 | 0.2 | 23.9 | 1100000
2023-11-21 | 40170 | 40.17 | 7.86 | 7.95 | 175 | 24 | 360 | 49 | 281 | 17 | NA | 600 | 0.3 | 23.89 | 1200000
2023-11-22 | 39030 | 39.03 | 7.81 | 7.88 | 170 | 25 | 356 | 46 | 269 | 20 | NA | 400 | 0.2 | 24.37 | 1100000
2023-11-23 | 38880 | 38.88 | 7.76 | 7.86 | 185 | 26 | 368 | 47 | 279 | 21 | NA | 700 | 0.2 | 23.99 | 1300000
2023-11-24 | 39120 | 39.12 | 7.88 | 7.92 | 185 | 28 | 370 | 48 | 268 | 18 | NA | 500 | 0.3 | 24.06 | 1100000
2023-11-25 | 39590 | 39.59 | 7.9 | 7.95 | 180 | 28 | 360 | 45 | 265 | 16 | NA | 600 | 0.3 | 25.07 | 1700000
2023-11-26 | 38840 | 38.84 | 7.85 | 7.89 | 180 | 29 | 355 | 41 | 285 | 20 | NA | 700 | 0.2 | 24.4 | 1200000
2023-11-27 | 39300 | 39.3 | 7.5 | 7.7 | 185 | 27 | 360 | 43 | 273 | 21 | NA | 600 | 0.2 | 23.86 | 1400000
2023-11-28 | 39780 | 39.78 | 7.8 | 7.89 | 195 | 26 | 365 | 45 | 270 | 22 | NA | 400 | 0.3 | 25.14 | 1700000
2023-11-29 | 39870 | 39.87 | 7.55 | 7.9 | 190 | 27 | 370 | 44 | 260 | 25 | NA | 400 | 0.3 | 24.05 | 1400000
2023-11-30 | 45310 | 45.31 | 7.86 | 7.91 | 185 | 28 | 368 | 48 | 273 | 29 | NA | 500 | 0.2 | 23.7 | 1400000
Average | 38925.6667 | 38.9257 | 7.738 | 7.8793 | 170.3333 | 22.7667 | 344.8333 | 44.3333 | 277 | 21.3333 | NA | 553.3333 | 0.24333 | 24.3487 | 1336666.6667
1167.77
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 36010 | 36.01 | 7.5 | 7.7 | 155 | 18 | 310 | 38 | 260 | 16 |  | 400 | 0.2 | 23.7 | 1100000
Max | 45310 | 45.31 | 7.9 | 7.95 | 195 | 29 | 370 | 49 | 293 | 29 |  | 700 | 0.3 | 25.2 | 1700000

## Phaphamau
Phaphamau STP, 14 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 14 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-11-01 | 15850 | 15.85 | 7.82 | 7.83 | 150 | 18 | 300 | 36 | 276 | 17 | NA | 600 | 0.2 | 23.41 | 1700000
2023-11-02 | 15520 | 15.52 | 7.75 | 7.82 | 160 | 20 | 312 | 44 | 274 | 16 | NA | 400 | 0.3 | 23.48 | 1400000
2023-11-03 | 14620 | 14.62 | 7.65 | 7.85 | 155 | 21 | 316 | 36 | 278 | 16 | NA | 500 | 0.2 | 23.24 | 1300000
2023-11-04 | 15150 | 15.15 | 7.59 | 7.82 | 160 | 20 | 312 | 44 | 265 | 17 | NA | 600 | 0.3 | 23.4 | 1700000
2023-11-05 | 16080 | 16.08 | 7.56 | 7.84 | 155 | 21 | 316 | 36 | 273 | 16 | NA | 400 | 0.2 | 23.32 | 1400000
2023-11-06 | 15390 | 15.39 | 7.6 | 7.88 | 160 | 20 | 308 | 44 | 275 | 15 | NA | 500 | 0.3 | 23.59 | 1300000
2023-11-07 | 15650 | 15.65 | 7.55 | 7.87 | 165 | 21 | 300 | 40 | 279 | 23 | NA | 600 | 0.2 | 23.58 | 1700000
2023-11-08 | 15760 | 15.76 | 7.65 | 7.82 | 160 | 20 | 308 | 44 | 290 | 17 | NA | 400 | 0.2 | 24.27 | 1400000
2023-11-09 | 14810 | 14.81 | 7.58 | 7.84 | 165 | 20 | 304 | 40 | 280 | 18 | NA | 500 | 0.3 | 22.08 | 1300000
2023-11-10 | 16800 | 16.8 | 7.62 | 7.86 | 155 | 21 | 292 | 44 | 300 | 16 | NA | 600 | 0.3 | 24.53 | 1400000
2023-11-11 | 16100 | 16.1 | 7.76 | 7.84 | 160 | 20 | 300 | 40 | 295 | 15 | NA | 400 | 0.2 | 23.83 | 1700000
2023-11-12 | 15670 | 15.67 | 7.75 | 7.84 | 155 | 21 | 287 | 44 | 285 | 14 | NA | 500 | 0.3 | 24.27 | 1300000
2023-11-13 | 14280 | 14.28 | 7.71 | 7.84 | 155 | 22 | 276 | 40 | 270 | 11 | NA | 400 | 0.2 | 23.9 | 1400000
2023-11-14 | 14220 | 14.22 | 7.72 | 7.83 | 160 | 22 | 292 | 44 | 290 | 10 | NA | 600 | 0.3 | 23.98 | 1700000
2023-11-15 | 14400 | 14.4 | 7.71 | 7.85 | 155 | 20 | 300 | 40 | 262 | 20 | NA | 500 | 0.2 | 23.52 | 1300000
2023-11-16 | 13990 | 13.99 | 7.72 | 7.85 | 160 | 22 | 304 | 44 | 248 | 21 | NA | 400 | 0.2 | 24.29 | 1700000
2023-11-17 | 13470 | 13.47 | 7.64 | 7.82 | 160 | 21 | 300 | 40 | 245 | 24 | NA | 500 | 0.3 | 22.73 | 1300000
2023-11-18 | 14540 | 14.54 | 7.64 | 7.84 | 155 | 22 | 304 | 44 | 240 | 23 | NA | 400 | 0.3 | 23.74 | 1400000
2023-11-19 | 14760 | 14.76 | 7.56 | 7.81 | 160 | 20 | 308 | 40 | 260 | 16 | NA | 600 | 0.2 | 23.31 | 1700000
2023-11-20 | 16100 | 16.1 | 7.52 | 7.84 | 160 | 22 | 316 | 44 | 248 | 25 | NA | 400 | 0.3 | 22.5 | 1300000
2023-11-21 | 15640 | 15.64 | 7.53 | 7.83 | 155 | 21 | 308 | 40 | 230 | 18 | NA | 600 | 0.2 | 24.53 | 1700000
2023-11-22 | 14540 | 14.54 | 7.52 | 7.85 | 160 | 20 | 300 | 36 | 250 | 19 | NA | 400 | 0.3 | 22.73 | 1300000
2023-11-23 | 14760 | 14.76 | 7.43 | 7.88 | 155 | 21 | 308 | 40 | 240 | 17 | NA | 600 | 0.3 | 22.73 | 1700000
2023-11-24 | 13950 | 13.95 | 7.4 | 7.84 | 165 | 20 | 304 | 36 | 245 | 16 | NA | 400 | 0.2 | 24.11 | 1400000
2023-11-25 | 14330 | 14.33 | 7.34 | 7.86 | 160 | 20 | 296 | 40 | 240 | 24 | NA | 500 | 0.3 | 24.29 | 1300000
2023-11-26 | 13750 | 13.75 | 7.35 | 7.85 | 165 | 20 | 304 | 36 | 260 | 25 | NA | 400 | 0.2 | 23.4 | 1700000
2023-11-27 | 14050 | 14.05 | 7.3 | 7.86 | 155 | 19 | 308 | 40 | 250 | 24 | NA | 500 | 0.2 | 24.53 | 1400000
2023-11-28 | 13050 | 13.05 | 7.28 | 7.88 | 160 | 19 | 304 | 40 | 260 | 15 | NA | 600 | 0.3 | 24.12 | 1300000
2023-11-29 | 14690 | 14.69 | 7.18 | 7.9 | 155 | 20 | 292 | 36 | 240 | 20 | NA | 400 | 0.2 | 23.79 | 1700000
2023-11-30 | 16780 | 16.78 | 7.07 | 7.85 | 160 | 18 | 304 | 40 | 290 | 26 | NA | 600 | 0.3 | 23.63 | 1300000
Average | 14956.6667 | 14.9567 | 7.55 | 7.8463 | 158.5 | 20.4 | 302.7667 | 40.4 | 264.6 | 18.4667 | NA | 493.3333 | 0.25 | 23.6277 | 1473333.3333
448.7
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 13050 | 13.05 | 7.07 | 7.81 | 150 | 18 | 276 | 36 | 230 | 10 |  | 400 | 0.2 | 22.08 | 1300000
Max | 16800 | 16.8 | 7.82 | 7.9 | 165 | 22 | 316 | 44 | 300 | 26 |  | 600 | 0.3 | 24.53 | 1700000

## Jhunsi
JHUNSI STP, 16 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 16 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-11-01 | 11350 | 11.35 | 7.84 | 7.78 | 155 | 13 | 260 | 44 | 223 | 14 | NA | 500 | 0.2 | - | - | 1. Sewage from 12 I&Ds is coming into SPS. 2. As the sewage received in STP was very dilute, sludge withdrawal from system was not started. Therefore, testing of sludge was not done. 3. Due to various issues in I&Ds, Trunk Sewer and overflow at I&D of Bhola Mandir Nalla & Savitri Nalla, sewage received from tapped I&Ds was less. 4. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2023-11-02 | 10840 | 10.84 | 7.91 | 7.67 | 160 | 15 | 265 | 46 | 230 | 16 | NA | 400 | 0.3 | 23.66 | 1100000 | From 02.11.2023 to 04.11.2023: 1. Sewage from 12 I&Ds is coming into SPS. 2. Sludge withdrawal from system was started from 02.11.2023. 3. Due to various issues in I&Ds, Trunk Sewer and overflow at I&D of Bhola Mandir Nalla & Savitri Nalla, sewage received from tapped I&Ds was less. 4. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2023-11-03 | 11800 | 11.8 | 7.81 | 7.76 | 165 | 18 | 276 | 41 | 235 | 18 | NA | 400 | 0.2 | 23.19 | 1400000
2023-11-04 | 11650 | 11.65 | 7.79 | 7.69 | 160 | 14 | 282 | 44 | 240 | 14 | NA | 400 | 0.2 | 23.73 | 1400000
2023-11-05 | 8540 | 8.54 | 7.83 | 7.78 | 155 | 17 | 296 | 46 | 265 | 17 | NA | 600 | 0.3 | 25.01 | 1700000 | From 05.11.2023 to 30.11.2023: 1. Sewage from 13 I&Ds started coming into SPS from 05.11.2023. 2. Due to various issues in I&Ds, Trunk Sewer and overflow at I&D of Bhola Mandir Nalla & Savitri Nalla, sewage received from tapped I&Ds was less. 3. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2023-11-06 | 10650 | 10.65 | 7.87 | 7.9 | 160 | 13 | 302 | 42 | 282 | 18 | NA | 500 | 0.2 | 24.52 | 1300000
2023-11-07 | 11080 | 11.08 | 7.92 | 7.7 | 165 | 19 | 310 | 44 | 286 | 14 | NA | 600 | 0.2 | 23.6 | 1400000
2023-11-08 | 10680 | 10.68 | 7.76 | 7.58 | 160 | 17 | 320 | 41.2 | 290 | 16 | NA | 500 | 0.2 | 24.44 | 1300000
2023-11-09 | 9060 | 9.06 | 7.89 | 7.91 | 165 | 16 | 334 | 46 | 296 | 17 | NA | 400 | 0.3 | 25.01 | 1100000
2023-11-10 | 14080 | 14.08 | 7.78 | 7.67 | 160 | 15 | 330 | 36 | 290 | 15 | NA | 400 | 0.2 | 24.69 | 1400000
2023-11-11 | 11950 | 11.95 | 7.84 | 7.68 | 155 | 14 | 316 | 40 | 295 | 18 | NA | 500 | 0.3 | 25.04 | 1300000
2023-11-12 | 10970 | 10.97 | 7.69 | 7.73 | 160 | 13 | 325 | 42 | 290 | 15 | NA | 400 | 0.3 | 24.09 | 1100000
2023-11-13 | 10540 | 10.54 | 7.76 | 7.87 | 165 | 17 | 330 | 38 | 280 | 17 | NA | 600 | 0.2 | 23.61 | 1400000
2023-11-14 | 10720 | 10.72 | 7.83 | 7.79 | 155 | 16 | 340 | 46 | 307 | 19 | NA | 500 | 0.3 | 23.76 | 1300000
2023-11-15 | 10780 | 10.78 | 7.75 | 7.81 | 160 | 14 | 335 | 44 | 310 | 18 | NA | 600 | 0.2 | 24.43 | 1700000
2023-11-16 | 11050 | 11.05 | 7.62 | 7.69 | 165 | 15 | 348 | 44 | 305 | 16 | NA | 500 | 0.2 | 24.6 | 1400000
2023-11-17 | 11560 | 11.56 | 7.73 | 7.76 | 155 | 17 | 344 | 42 | 310 | 19 | NA | 400 | 0.2 | 23.77 | 1100000
2023-11-18 | 10380 | 10.38 | 7.67 | 7.74 | 160 | 18 | 340 | 40 | 301 | 17 | NA | 700 | 0.3 | 24.1 | 1700000
2023-11-19 | 10540 | 10.54 | 7.83 | 7.79 | 165 | 15 | 338 | 41 | 307 | 15 | NA | 600 | 0.3 | 23.86 | 1300000
2023-11-20 | 10260 | 10.26 | 7.92 | 7.87 | 160 | 14 | 330 | 38 | 306 | 16 | NA | 400 | 0.2 | 24.5 | 1400000
2023-11-21 | 10230 | 10.23 | 7.54 | 7.37 | 155 | 12 | 336 | 40 | 310 | 13 | NA | 500 | 0.3 | 23.56 | 1100000
2023-11-22 | 10580 | 10.58 | 7.83 | 7.79 | 160 | 15 | 342 | 44 | 312 | 15 | NA | 400 | 0.3 | 24.48 | 1300000
2023-11-23 | 10670 | 10.67 | 7.54 | 7.61 | 165 | 18 | 340 | 46 | 308 | 14 | NA | 500 | 0.2 | 23.5 | 1400000
2023-11-24 | 11130 | 11.13 | 7.63 | 7.67 | 155 | 16 | 344 | 42 | 314 | 17 | NA | 600 | 0.3 | 24.56 | 1100000
2023-11-25 | 11560 | 11.56 | 7.79 | 7.83 | 160 | 14 | 340 | 40 | 308 | 16 | NA | 500 | 0.2 | 23.6 | 1400000
2023-11-26 | 12640 | 12.64 | 7.83 | 7.79 | 165 | 17 | 342 | 44 | 312 | 19 | NA | 400 | 0.3 | 24.26 | 1300000
2023-11-27 | 11880 | 11.88 | 7.94 | 7.62 | 160 | 15 | 346 | 42 | 323 | 15 | NA | 700 | 0.3 | 23.73 | 1700000
2023-11-28 | 12160 | 12.16 | 7.75 | 7.35 | 155 | 19 | 344 | 40 | 314 | 18 | NA | 500 | 0.3 | 24.22 | 1400000
2023-11-29 | 12080 | 12.08 | 7.71 | 7.46 | 160 | 14 | 342 | 46 | 318 | 14 | NA | 400 | 0.2 | 23.64 | 1200000
2023-11-30 | 10380 | 10.38 | 7.67 | 7.78 | 155 | 18 | 348 | 44 | 310 | 16 | NA | 600 | 0.3 | 24.48 | 1100000
Average | 11059.6667 | 11.0597 | 7.7757 | 7.7147 | 159.8333 | 15.6 | 324.8333 | 42.44 | 292.5667 | 16.2 | NA | 500 | 0.25 | 24.1255 | 1337931.0345
331.79
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 8540 | 8.54 | 7.54 | 7.35 | 155 | 12 | 260 | 36 | 223 | 13 |  | 400 | 0.2 | 23.19 | 1100000
Max | 14080 | 14.08 | 7.94 | 7.91 | 165 | 19 | 348 | 46 | 323 | 19 |  | 700 | 0.3 | 25.04 | 1700000