## Naini-2
Naini-2 STP, 42 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 42 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-10-01 | 41740 | 41.74 | 7.61 | 7.93 | 155 | 22 | 320 | 40 | 289 | 24 | NA | 700 | 0.2 | 23.77 | 1700000
2023-10-02 | 49620 | 49.62 | 7.68 | 7.98 | 160 | 20 | 346 | 41 | 294 | 25 | NA | 600 | 0.2 | 24.31 | 1300000
2023-10-03 | 40880 | 40.88 | 7.59 | 7.89 | 155 | 22 | 314 | 42 | 277 | 23 | NA | 400 | 0.3 | 25.44 | 1700000
2023-10-04 | 42000 | 42 | 7.72 | 7.87 | 165 | 23 | 310 | 44 | 264 | 25 | NA | 700 | 0.3 | 24.8 | 1400000
2023-10-05 | 40810 | 40.81 | 7.7 | 7.92 | 160 | 24 | 326 | 46 | 259 | 24 | NA | 500 | 0.2 | 25.12 | 1700000
2023-10-06 | 40790 | 40.79 | 7.61 | 7.93 | 155 | 20 | 321 | 44 | 266 | 22 | NA | 700 | 0.2 | 24.51 | 1300000
2023-10-07 | 39720 | 39.72 | 7.72 | 7.91 | 165 | 17 | 320 | 38 | 282 | 20 | NA | 400 | 0.2 | 23.9 | 1100000
2023-10-08 | 42710 | 42.71 | 7.75 | 7.94 | 160 | 19 | 328 | 36 | 270 | 23 | NA | 600 | 0.2 | 25.11 | 1400000
2023-10-09 | 39900 | 39.9 | 7.76 | 7.93 | 165 | 22 | 314 | 42 | 261 | 21 | NA | 500 | 0.3 | 24.2 | 1200000
2023-10-10 | 38620 | 38.62 | 7.73 | 7.95 | 155 | 23 | 326 | 46 | 268 | 22 | NA | 600 | 0.2 | 24.5 | 1700000
2023-10-11 | 40190 | 40.19 | 7.59 | 7.97 | 160 | 21 | 328 | 42 | 285 | 23 | NA | 400 | 0.2 | 25.01 | 1400000
2023-10-12 | 38150 | 38.15 | 7.7 | 7.96 | 155 | 22 | 322 | 44 | 274 | 21 | NA | 500 | 0.3 | 24.7 | 1100000
2023-10-13 | 38870 | 38.87 | 7.69 | 7.99 | 165 | 23 | 336 | 45 | 280 | 20 | NA | 600 | 0.2 | 24.57 | 1300000
2023-10-14 | 39650 | 39.65 | 7.5 | 7.91 | 160 | 25 | 318 | 48 | 268 | 22 | NA | 400 | 0.2 | 25.14 | 1700000
2023-10-15 | 39290 | 39.29 | 7.66 | 7.9 | 155 | 24 | 305 | 49 | 257 | 26 | NA | 700 | 0.3 | 23.95 | 1400000
2023-10-16 | 41230 | 41.23 | 7.53 | 7.94 | 160 | 23 | 324 | 46 | 270 | 24 | NA | 600 | 0.3 | 24.5 | 1200000
2023-10-17 | 36600 | 36.6 | 7.68 | 7.97 | 165 | 24 | 334 | 48 | 287 | 22 | NA | 700 | 0.2 | 24.12 | 1400000
2023-10-18 | 37420 | 37.42 | 7.7 | 7.94 | 160 | 22 | 344 | 44 | 282 | 21 | NA | 400 | 0.2 | 25.1 | 1300000
2023-10-19 | 37460 | 37.46 | 7.74 | 7.97 | 165 | 24 | 348 | 46 | 290 | 23 | NA | 600 | 0.3 | 23.88 | 1700000
2023-10-20 | 39900 | 39.9 | 7.8 | 7.94 | 160 | 23 | 324 | 45 | 278 | 24 | NA | 700 | 0.2 | 24.24 | 1100000
2023-10-21 | 35410 | 35.41 | 7.74 | 7.89 | 155 | 21 | 318 | 42 | 280 | 22 | NA | 500 | 0.2 | 25.07 | 1400000
2023-10-22 | 37880 | 37.88 | 7.76 | 7.92 | 160 | 22 | 324 | 44 | 268 | 20 | NA | 400 | 0.3 | 24.64 | 1700000
2023-10-23 | 37820 | 37.82 | 7.73 | 7.9 | 165 | 23 | 332 | 46 | 283 | 23 | NA | 600 | 0.2 | 23.95 | 1300000
2023-10-24 | 38490 | 38.49 | 7.71 | 7.89 | 160 | 24 | 320 | 48 | 278 | 20 | NA | 400 | 0.2 | 24.57 | 1400000
2023-10-25 | 36750 | 36.75 | 7.69 | 7.88 | 155 | 23 | 312 | 47 | 264 | 22 | NA | 500 | 0.3 | 25.16 | 1300000
2023-10-26 | 38020 | 38.02 | 7.67 | 7.89 | 160 | 21 | 316 | 48 | 260 | 19 | NA | 400 | 0.3 | 24.31 | 1700000
2023-10-27 | 37780 | 37.78 | 7.7 | 7.91 | 155 | 20 | 322 | 46 | 266 | 18 | NA | 600 | 0.2 | 24.5 | 1400000
2023-10-28 | 36860 | 36.86 | 7.74 | 7.93 | 160 | 19 | 324 | 44 | 279 | 17 | NA | 400 | 0.2 | 23.9 | 1100000
2023-10-29 | 38260 | 38.26 | 7.76 | 7.89 | 165 | 20 | 334 | 46 | 264 | 19 | NA | 500 | 0.3 | 24.58 | 1200000
2023-10-30 | 37190 | 37.19 | 7.7 | 7.87 | 160 | 22 | 326 | 48 | 286 | 18 | NA | 600 | 0.2 | 25.1 | 1700000
2023-10-31 | 36510 | 36.51 | 7.69 | 7.84 | 155 | 23 | 320 | 46 | 279 | 22 | NA | 700 | 0.2 | 24.77 | 1400000
Average | 39242.5806 | 39.2426 | 7.6887 | 7.921 | 159.6774 | 21.9677 | 324.3871 | 44.5484 | 274.4516 | 21.7742 |  | 545.1613 | 0.23548 | 24.5619 | 1409677.4194
1216.52
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 35410 | 35.41 | 7.5 | 7.84 | 155 | 17 | 305 | 36 | 257 | 17 |  | 400 | 0.2 | 23.77 | 1100000
Max | 49620 | 49.62 | 7.8 | 7.99 | 165 | 25 | 348 | 49 | 294 | 26 |  | 700 | 0.3 | 25.44 | 1700000

## Phaphamau
Phaphamau STP, 14 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 14 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-10-01 | 17310 | 17.31 | 7.36 | 8.1 | 160 | 26 | 320 | 44 | 265 | 26 | NA | 500 | 0.3 | 22.73 | 1300000
2023-10-02 | 20820 | 20.82 | 7.21 | 8.06 | 165 | 28 | 304 | 48 | 325 | 28 | NA | 600 | 0.2 | 23.74 | 1400000
2023-10-03 | 17490 | 17.49 | 7.3 | 8.08 | 150 | 26 | 308 | 48 | 270 | 30 | NA | 400 | 0.2 | 22.05 | 1700000
2023-10-04 | 21060 | 21.06 | 7.25 | 7.91 | 160 | 28 | 320 | 44 | 240 | 20 | NA | 500 | 0.3 | 24.55 | 1400000
2023-10-05 | 17040 | 17.04 | 7.2 | 7.69 | 180 | 26 | 368 | 44 | 275 | 18 | NA | 600 | 0.2 | 23.84 | 1700000
2023-10-06 | 17330 | 17.33 | 7.21 | 7.72 | 165 | 26 | 352 | 44 | 307 | 19 | NA | 400 | 0.3 | 24.98 | 1300000
2023-10-07 | 18470 | 18.47 | 7.16 | 7.7 | 155 | 24 | 320 | 48 | 265 | 15 | NA | 600 | 0.2 | 24.53 | 1700000
2023-10-08 | 19470 | 19.47 | 7.17 | 7.72 | 165 | 26 | 324 | 44 | 240 | 16 | NA | 500 | 0.2 | 23.2 | 1400000
2023-10-09 | 18110 | 18.11 | 7.22 | 7.69 | 160 | 24 | 320 | 48 | 250 | 17 | NA | 400 | 0.3 | 23.96 | 1300000
2023-10-10 | 16880 | 16.88 | 7.21 | 7.7 | 165 | 25 | 316 | 44 | 280 | 20 | NA | 600 | 0.2 | 22.73 | 1700000
2023-10-11 | 16070 | 16.07 | 7.19 | 7.73 | 160 | 26 | 304 | 48 | 305 | 22 | NA | 400 | 0.2 | 24.29 | 1400000
2023-10-12 | 15290 | 15.29 | 7.18 | 7.72 | 155 | 27 | 308 | 44 | 270 | 18 | NA | 500 | 0.3 | 22.58 | 1300000
2023-10-13 | 15890 | 15.89 | 7.29 | 7.74 | 155 | 26 | 320 | 48 | 305 | 16 | NA | 400 | 0.2 | 23.74 | 1700000
2023-10-14 | 16290 | 16.29 | 7.26 | 7.75 | 160 | 24 | 316 | 44 | 290 | 19 | NA | 500 | 0.2 | 23.02 | 1400000
2023-10-15 | 16320 | 16.32 | 7.27 | 7.74 | 165 | 25 | 320 | 48 | 315 | 19 | NA | 400 | 0.3 | 23.46 | 1700000
2023-10-16 | 16290 | 16.29 | 7.15 | 7.75 | 160 | 24 | 304 | 44 | 290 | 16 | NA | 600 | 0.2 | 22.93 | 1300000
2023-10-17 | 15690 | 15.69 | 7.3 | 7.5 | 150 | 25 | 440 | 32 | 290 | 14 | NA | 500 | 0.2 | 24.53 | 1400000
2023-10-18 | 16660 | 16.66 | 7.2 | 7.77 | 155 | 26 | 308 | 44 | 273 | 13 | NA | 400 | 0.3 | 23.07 | 1300000
2023-10-19 | 14960 | 14.96 | 7.22 | 7.79 | 160 | 25 | 304 | 48 | 285 | 14 | NA | 600 | 0.2 | 24.54 | 1700000
2023-10-20 | 14670 | 14.67 | 7.25 | 7.78 | 155 | 27 | 272 | 44 | 230 | 15 | NA | 400 | 0.3 | 23.47 | 1400000
2023-10-21 | 15740 | 15.74 | 7.46 | 7.8 | 160 | 23 | 280 | 44 | 280 | 16 | NA | 600 | 0.2 | 24.19 | 1700000
2023-10-22 | 14340 | 14.34 | 7.69 | 7.81 | 160 | 18 | 272 | 36 | 270 | 15 | NA | 500 | 0.2 | 22.79 | 1300000
2023-10-23 | 15260 | 15.26 | 7.64 | 7.81 | 155 | 20 | 280 | 40 | 271 | 14 | NA | 400 | 0.3 | 24.54 | 1400000
2023-10-24 | 15540 | 15.54 | 7.62 | 7.85 | 155 | 22 | 260 | 36 | 275 | 15 | NA | 500 | 0.2 | 22.58 | 1300000
2023-10-25 | 14970 | 14.97 | 7.6 | 7.82 | 150 | 19 | 272 | 40 | 250 | 13 | NA | 600 | 0.3 | 24.34 | 1700000
2023-10-26 | 14630 | 14.63 | 7.7 | 7.85 | 160 | 18 | 288 | 36 | 260 | 16 | NA | 400 | 0.2 | 24.53 | 1400000
2023-10-27 | 15210 | 15.21 | 7.66 | 7.85 | 165 | 19 | 324 | 36 | 285 | 17 | NA | 600 | 0.3 | 22.88 | 1300000
2023-10-28 | 16050 | 16.05 | 7.7 | 7.85 | 160 | 18 | 288 | 40 | 262 | 17 | NA | 500 | 0.2 | 23.37 | 1700000
2023-10-29 | 15270 | 15.27 | 7.63 | 7.84 | 155 | 19 | 304 | 36 | 262 | 19 | NA | 400 | 0.3 | 23.02 | 1300000
2023-10-30 | 15240 | 15.24 | 7.53 | 7.81 | 165 | 18 | 296 | 40 | 259 | 15 | NA | 600 | 0.2 | 23.17 | 1400000
2023-10-31 | 15610 | 15.61 | 7.64 | 7.85 | 155 | 19 | 292 | 40 | 257 | 15 | NA | 500 | 0.3 | 23.13 | 1300000
Average | 16450.6452 | 16.4506 | 7.37 | 7.7994 | 159.3548 | 23.4516 | 309.8065 | 42.7097 | 274.2258 | 17.6452 |  | 496.7742 | 0.24194 | 23.5639 | 1461290.3226
509.97
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 14340 | 14.34 | 7.15 | 7.5 | 150 | 18 | 260 | 32 | 230 | 13 |  | 400 | 0.2 | 22.05 | 1300000
Max | 21060 | 21.06 | 7.7 | 8.1 | 180 | 28 | 440 | 48 | 325 | 30 |  | 600 | 0.3 | 24.98 | 1700000

## Jhunsi
JHUNSI STP, 16 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 16 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-10-01 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | - | From 01.10.2023 to 02.10.2023: 1. Water started receding in river Ganga from 27.09.2023 and most of the I&Ds were free from river water by 28.08.2023.However, pumping from Shastri Bridge SPS is not started as the cleaning of silt & mud deposited in I&Ds, cleaning of choked pipes was in progress. 2. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2023-10-02 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-10-03 | 2410 | 2.41 | - | - | - | - | - | - | - | - | NA | - | 0.2 | - | - | From 03.10.2023 to 04.10.2023: 1. Sewage from 3 I&Ds started coming into SPS and further pumping started to Jhunsi STP from 2:38 PM 2. At Jhunsi STP, sewage was bypassed after PTU due to excessive amount of silt and mud. 3. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2023-10-04 | 4780 | 4.78 | - | - | - | - | - | - | - | - | NA | - | 0.2 | - | -
2023-10-05 | 5380 | 5.38 | 7.92 | 8.01 | 40 | 35 | 102 | 91 | 68 | 60 | NA | - | 0.2 | - | - | From 05.10.2023 to 13.10.2023: 1. Sewage from 6 I&Ds started coming into SPS from 05.10.2023. 2. Sewage from 7 I&Ds started coming into SPS from 06.10.2023. 3. Sewage from 8 I&Ds started coming into SPS from 07.10.2023. 4. Sewage from 9 I&Ds started coming into SPS from 10.10.2023. 5. Sewage from 10 I&Ds started coming into SPS from 11.10.2023. 6. Due to various issues in I&Ds, Trunk Sewer and overflow at I&D of Bhola Mandir Nalla & Savitri Nalla, sewage received from tapped I&Ds was less. 7. At Jhunsi STP, sewage was bypassed after PTU due to excessive amount of silt and mud. Therefore, KPIs are out of range. 8. As the sewage received in STP was very dilute, sludge withdrawal from system was not started. Therefore, testing of sludge was not done. 9. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2023-10-06 | 5290 | 5.29 | 7.83 | 7.99 | 36 | 31 | 97 | 87 | 57 | 57 | NA | - | 0.2 | - | -
2023-10-07 | 5290 | 5.29 | 7.77 | 7.91 | 43 | 38 | 114 | 101 | 78 | 70 | NA | - | 0.2 | - | -
2023-10-08 | 5620 | 5.62 | 7.86 | 7.94 | 34 | 30 | 89 | 80 | 54 | 46 | NA | - | 0.2 | - | -
2023-10-09 | 5460 | 5.46 | 7.74 | 7.86 | 48 | 42 | 102 | 91 | 76 | 62 | NA | - | 0.2 | - | -
2023-10-10 | 5700 | 5.7 | 7.77 | 7.86 | 45 | 40 | 121 | 104 | 83 | 75 | NA | - | 0.2 | - | -
2023-10-11 | 4870 | 4.87 | 7.89 | 8 | 38 | 32 | 94 | 83 | 61 | 54 | NA | - | 0.2 | - | -
2023-10-12 | 4880 | 4.88 | 7.73 | 7.79 | 50 | 29 | 112 | 92 | 82 | 53 | NA | - | 0.2 | - | -
2023-10-13 | 4640 | 4.64 | 7.79 | 7.82 | 55 | 22 | 116 | 88 | 81 | 56 | NA | 700 | 0.2 | - | - | From 13.10.2023 to 19.10.2023: 1. Treatment in FCRs & Tubesettlers is started from 13.10.2023. 2. Sewage from 10 I&Ds is coming into SPS. 3. As the sewage received in STP was very dilute, sludge withdrawal from system was not started. Therefore, testing of sludge was not done. 4. Due to various issues in I&Ds, Trunk Sewer and overflow at I&D of Bhola Mandir Nalla & Savitri Nalla, sewage received from tapped I&Ds was less. 5. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2023-10-14 | 4960 | 4.96 | 7.56 | 7.86 | 65 | 24 | 108 | 86 | 79 | 49 | NA | 600 | 0.3 | - | -
2023-10-15 | 4330 | 4.33 | 7.55 | 7.85 | 60 | 28 | 120 | 94 | 85 | 58 | NA | 400 | 0.4 | - | -
2023-10-16 | 5090 | 5.09 | 7.62 | 7.79 | 60 | 30 | 135 | 35 | 92 | 18 | NA | 700 | 0.3 | - | -
2023-10-17 | 5730 | 5.73 | 7.53 | 7.71 | 75 | 25 | 140 | 38 | 104 | 16 | NA | 500 | 0.3 | - | -
2023-10-18 | 5780 | 5.78 | 7.65 | 7.82 | 90 | 25 | 122 | 28 | 96 | 14 | NA | 400 | 0.4 | - | -
2023-10-19 | 6060 | 6.06 | 7.54 | 7.9 | 95 | 20 | 128 | 30 | 108 | 12 | NA | 600 | 0.3 | - | -
2023-10-20 | 8330 | 8.33 | 7.32 | 7.54 | 120 | 25 | 230 | 42 | 168 | 14 | NA | 500 | 0.3 | - | - | From 20.10.2023 to 31.10.2023: 1. Sewage from 12 I&Ds started coming into SPS from 20.10.2023. 2. As the sewage received in STP was very dilute, sludge withdrawal from system was not started. Therefore, testing of sludge was not done. 3. Due to various issues in I&Ds, Trunk Sewer and overflow at I&D of Bhola Mandir Nalla & Savitri Nalla, sewage received from tapped I&Ds was less. 4. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2023-10-21 | 13210 | 13.21 | 7.83 | 7.21 | 140 | 20 | 222 | 38 | 154 | 16 | NA | 400 | 0.4 | - | -
2023-10-22 | 14340 | 14.34 | 7.73 | 7.61 | 148 | 20 | 240 | 42 | 164 | 10 | NA | 400 | 0.3 | - | -
2023-10-23 | 13290 | 13.29 | 7.76 | 7.72 | 155 | 13 | 255 | 40 | 178 | 12 | NA | 500 | 0.3 | - | -
2023-10-24 | 12210 | 12.21 | 7.73 | 7.76 | 160 | 19.5 | 260 | 38 | 186 | 14 | NA | 400 | 0.4 | - | -
2023-10-25 | 12250 | 12.25 | 7.57 | 7.56 | 155 | 18 | 245 | 35 | 194 | 12 | NA | 400 | 0.3 | - | -
2023-10-26 | 12560 | 12.56 | 7.82 | 7.79 | 165 | 17 | 260 | 40 | 198 | 14 | NA | 500 | 0.3 | - | -
2023-10-27 | 11420 | 11.42 | 7.92 | 7.54 | 155 | 15 | 264 | 48.8 | 200 | 16 | NA | 400 | 0.4 | - | -
2023-10-28 | 10720 | 10.72 | 7.53 | 7.71 | 155 | 17 | 228 | 42 | 214 | 15 | NA | 500 | 0.4 | - | -
2023-10-29 | 11610 | 11.61 | 7.76 | 7.72 | 160 | 15 | 201.2 | 46.4 | 210 | 17 | NA | 500 | 0.3 | - | -
2023-10-30 | 11720 | 11.72 | 7.83 | 7.61 | 165 | 15 | 220 | 40.4 | 195 | 12 | NA | 400 | 0.3 | - | -
2023-10-31 | 11170 | 11.17 | 7.9 | 7.72 | 160 | 14 | 210 | 42 | 206 | 19 | NA | 400 | 0.2 | - | -
Average | 7390.3226 | 7.3903 | 7.7204 | 7.763 | 98.963 | 24.4259 | 167.9704 | 60.0963 | 128.5556 | 32.2593 |  | 484.2105 | 0.27931 | - | -
229.1
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 7.32 | 7.21 | 34 | 13 | 89 | 28 | 54 | 10 |  | 400 | 0.2 | 0 | 0
Max | 14340 | 14.34 | 7.92 | 8.01 | 165 | 42 | 264 | 104 | 214 | 75 |  | 700 | 0.4 | 0 | 0