## Naini-2
Naini-2 STP, 42 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 25 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-09-01 | 47070 | 47.07 | 7.55 | 7.84 | 170 | 23 | 346 | 45 | 271 | 22 | NA | 700 | 0.3 | 24.51 | 1200000
2023-09-02 | 42990 | 42.99 | 7.53 | 7.87 | 175 | 20 | 336 | 40 | 261 | 20 | NA | 500 | 0.3 | 23.87 | 1400000
2023-09-03 | 42420 | 42.42 | 7.49 | 7.79 | 170 | 22 | 360 | 47 | 278 | 18 | NA | 400 | 0.2 | 24.61 | 1700000
2023-09-04 | 42680 | 42.68 | 7.61 | 7.87 | 165 | 23 | 342 | 48 | 259 | 20 | NA | 600 | 0.3 | 25.03 | 1300000
2023-09-05 | 45170 | 45.17 | 7.58 | 7.89 | 160 | 22 | 330 | 46 | 263 | 19 | NA | 400 | 0.3 | 24.3 | 1100000
2023-09-06 | 45220 | 45.22 | 7.63 | 7.88 | 165 | 24 | 334 | 48 | 269 | 18 | NA | 600 | 0.2 | 24.81 | 1400000
2023-09-07 | 52910 | 52.91 | 7.59 | 7.81 | 160 | 25 | 340 | 47 | 282 | 23 | NA | 500 | 0.3 | 25.96 | 1200000
2023-09-08 | 62630 | 62.63 | 7.54 | 7.83 | 165 | 23 | 346 | 45 | 272 | 25 | NA | 600 | 0.3 | 24.7 | 1400000
2023-09-09 | 54760 | 54.76 | 7.51 | 7.8 | 170 | 24 | 350 | 44 | 280 | 22 | NA | 700 | 0.2 | 23.75 | 1700000
2023-09-10 | 53330 | 53.33 | 7.58 | 7.82 | 175 | 25 | 330 | 46 | 287 | 19 | NA | 500 | 0.3 | 25.13 | 1400000
2023-09-11 | 49100 | 49.1 | 7.55 | 7.9 | 160 | 22 | 311 | 44 | 266 | 16 | NA | 400 | 0.2 | 23.8 | 1300000
2023-09-12 | 47050 | 47.05 | 7.61 | 7.88 | 170 | 23 | 334 | 46 | 273 | 15 | NA | 500 | 0.3 | 24.51 | 1100000
2023-09-13 | 53390 | 53.39 | 7.54 | 7.9 | 175 | 24 | 322 | 48 | 285 | 17 | NA | 600 | 0.3 | 25.07 | 1400000
2023-09-14 | 46810 | 46.81 | 7.62 | 7.89 | 155 | 25 | 310 | 47 | 270 | 15 | NA | 700 | 0.2 | 24.11 | 1300000
2023-09-15 | 49180 | 49.18 | 7.68 | 7.87 | 160 | 23 | 328 | 48 | 280 | 16 | NA | 400 | 0.3 | 23.78 | 1200000
2023-09-16 | 46850 | 46.85 | 7.7 | 7.9 | 175 | 20 | 334 | 44 | 272 | 14 | NA | 500 | 0.2 | 24.5 | 1700000
2023-09-17 | 51070 | 51.07 | 7.69 | 7.92 | 180 | 21 | 368 | 46 | 298 | 15 | NA | 400 | 0.3 | 24.33 | 1400000
2023-09-18 | 57800 | 57.8 | 7.57 | 7.89 | 175 | 20 | 348 | 44 | 290 | 17 | NA | 600 | 0.3 | 25.08 | 1100000
2023-09-19 | 47180 | 47.18 | 7.54 | 7.81 | 170 | 22 | 332 | 47 | 268 | 18 | NA | 400 | 0.2 | 25.3 | 1300000
2023-09-20 | 35110 | 35.11 | 7.64 | 7.83 | 160 | 23 | 323 | 46 | 284 | 19 | NA | 500 | 0.3 | 23.78 | 1200000
2023-09-21 | 39130 | 39.13 | 7.62 | 7.94 | 175 | 21 | 338 | 45 | 289 | 20 | NA | 600 | 0.3 | 25.22 | 1700000
2023-09-22 | 39460 | 39.46 | 7.6 | 7.95 | 170 | 20 | 346 | 44 | 301 | 19 | NA | 400 | 0.2 | 24.38 | 1300000
2023-09-23 | 37450 | 37.45 | 7.66 | 7.94 | 160 | 21 | 327 | 43 | 281 | 20 | NA | 500 | 0.2 | 24.7 | 1100000
2023-09-24 | 39570 | 39.57 | 7.57 | 7.91 | 165 | 20 | 320 | 46 | 271 | 18 | NA | 600 | 0.3 | 23.77 | 1400000
2023-09-25 | 37120 | 37.12 | 7.71 | 7.97 | 170 | 21 | 320 | 44 | 286 | 17 | NA | 400 | 0.2 | 24.17 | 1200000
2023-09-26 | 38550 | 38.55 | 7.68 | 7.95 | 160 | 20 | 330 | 42 | 280 | 17 | NA | 500 | 0.2 | 25.02 | 1700000
2023-09-27 | 39870 | 39.87 | 7.7 | 7.97 | 155 | 22 | 326 | 46 | 288 | 20 | NA | 600 | 0.3 | 24.37 | 1300000
2023-09-28 | 37650 | 37.65 | 7.67 | 7.96 | 160 | 24 | 340 | 45 | 284 | 24 | NA | 700 | 0.3 | 24.3 | 1100000
2023-09-29 | 39980 | 39.98 | 7.63 | 7.98 | 155 | 23 | 314 | 42 | 268 | 22 | NA | 500 | 0.2 | 24.21 | 1400000
2023-09-30 | 38300 | 38.3 | 7.7 | 7.96 | 160 | 24 | 342 | 46 | 300 | 23 | NA | 600 | 0.2 | 25.4 | 1200000
Average | 45326.6667 | 45.3267 | 7.6097 | 7.8907 | 166.1667 | 22.3333 | 334.2333 | 45.3 | 278.5333 | 18.9333 |  | 530 | 0.25667 | 24.549 | 1340000
1359.8
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 35110 | 35.11 | 7.49 | 7.79 | 155 | 20 | 310 | 40 | 259 | 14 |  | 400 | 0.2 | 23.75 | 1100000
Max | 62630 | 62.63 | 7.71 | 7.98 | 180 | 25 | 368 | 48 | 301 | 25 |  | 700 | 0.3 | 25.96 | 1700000

## Phaphamau
Phaphamau STP, 14 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 10 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-09-01 | 14350 | 14.35 | 6.65 | 7.71 | 185 | 22 | 360 | 40 | 335 | 23 | NA | 400 | 0.2 | 23.58 | 1700000
2023-09-02 | 13680 | 13.68 | 7.85 | 7.92 | 180 | 20 | 364 | 36 | 280 | 23 | NA | 600 | 0.3 | 24.53 | 1400000
2023-09-03 | 12760 | 12.76 | 7.83 | 7.95 | 170 | 23 | 360 | 40 | 315 | 20 | NA | 700 | 0.2 | 23.02 | 1700000
2023-09-04 | 14470 | 14.47 | 7.92 | 7.94 | 185 | 24 | 364 | 36 | 280 | 21 | NA | 400 | 0.3 | 23.23 | 1300000
2023-09-05 | 13730 | 13.73 | 7.87 | 8.03 | 170 | 22 | 360 | 40 | 290 | 17 | NA | 600 | 0.2 | 24.27 | 1700000
2023-09-06 | 14600 | 14.6 | 7.82 | 8.02 | 175 | 23 | 364 | 36 | 291 | 18 | NA | 400 | 0.3 | 22.97 | 1300000
2023-09-07 | 17150 | 17.15 | 7.78 | 8.04 | 165 | 24 | 360 | 40 | 310 | 20 | NA | 600 | 0.2 | 24.53 | 1700000
2023-09-08 | 17590 | 17.59 | 7.76 | 8.05 | 160 | 21 | 364 | 40 | 290 | 21 | NA | 500 | 0.3 | 24.55 | 1400000
2023-09-09 | 17630 | 17.63 | 7.76 | 8.01 | 165 | 24 | 368 | 44 | 240 | 20 | NA | 600 | 0.2 | 23.83 | 1700000
2023-09-10 | 18740 | 18.74 | 8.31 | 8.66 | 175 | 24 | 340 | 40 | 220 | 22 | NA | 400 | 0.3 | 24.53 | 1300000
2023-09-11 | 17280 | 17.28 | 7.63 | 8.03 | 170 | 22 | 360 | 44 | 250 | 21 | NA | 600 | 0.2 | 23.91 | 1700000
2023-09-12 | 16690 | 16.69 | 8.2 | 8.7 | 175 | 24 | 340 | 40 | 300 | 18 | NA | 400 | 0.3 | 22.73 | 1300000
2023-09-13 | 18870 | 18.87 | 7.7 | 8.04 | 165 | 22 | 372 | 44 | 250 | 19 | NA | 500 | 0.2 | 24.55 | 1700000
2023-09-14 | 18050 | 18.05 | 7.54 | 8.02 | 170 | 24 | 364 | 40 | 245 | 16 | NA | 600 | 0.3 | 23.9 | 1300000
2023-09-15 | 16910 | 16.91 | 7.55 | 7.83 | 180 | 23 | 376 | 44 | 260 | 17 | NA | 500 | 0.2 | 23.71 | 1700000
2023-09-16 | 17510 | 17.51 | 7.59 | 7.95 | 170 | 24 | 340 | 40 | 300 | 18 | NA | 400 | 0.3 | 23.74 | 1400000
2023-09-17 | 19160 | 19.16 | 7.56 | 7.78 | 175 | 25 | 332 | 44 | 275 | 20 | NA | 600 | 0.2 | 22.29 | 1700000
2023-09-18 | 17750 | 17.75 | 7.7 | 7.83 | 170 | 24 | 324 | 40 | 250 | 24 | NA | 500 | 0.3 | 24.55 | 1300000
2023-09-19 | 17090 | 17.09 | 7.09 | 7.91 | 175 | 25 | 328 | 44 | 230 | 18 | NA | 600 | 0.2 | 24.21 | 1700000
2023-09-20 | 16400 | 16.4 | 7.92 | 8.1 | 180 | 23 | 336 | 40 | 260 | 21 | NA | 400 | 0.3 | 22.87 | 1400000
2023-09-21 | 19440 | 19.44 | 7.69 | 8.03 | 175 | 24 | 340 | 44 | 220 | 26 | NA | 500 | 0.2 | 22.73 | 1300000
2023-09-22 | 16800 | 16.8 | 7.93 | 8.07 | 185 | 23 | 368 | 40 | 256 | 24 | NA | 600 | 0.3 | 23.41 | 1700000
2023-09-23 | 16450 | 16.45 | 7.71 | 8.1 | 165 | 24 | 316 | 44 | 260 | 26 | NA | 400 | 0.2 | 24.23 | 1300000
2023-09-24 | 17800 | 17.8 | 7.92 | 8.12 | 160 | 22 | 304 | 40 | 264 | 27 | NA | 600 | 0.3 | 22.83 | 1700000
2023-09-25 | 17770 | 17.77 | 7.9 | 8.09 | 165 | 24 | 324 | 40 | 260 | 21 | NA | 500 | 0.3 | 24.29 | 1300000
2023-09-26 | 18580 | 18.58 | 7.55 | 8.1 | 170 | 26 | 320 | 44 | 270 | 26 | NA | 700 | 0.2 | 23.79 | 1700000
2023-09-27 | 18150 | 18.15 | 7.9 | 8.05 | 160 | 28 | 316 | 40 | 255 | 23 | NA | 600 | 0.3 | 24.53 | 1400000
2023-09-28 | 16630 | 16.63 | 7.32 | 7.83 | 155 | 27 | 300 | 44 | 252 | 28 | NA | 500 | 0.3 | 23.2 | 1300000
2023-09-29 | 14830 | 14.83 | 7.92 | 8.06 | 160 | 28 | 324 | 40 | 240 | 20 | NA | 700 | 0.2 | 23.46 | 1700000
2023-09-30 | 15980 | 15.98 | 7.6 | 8.11 | 155 | 26 | 272 | 44 | 260 | 33 | NA | 600 | 0.3 | 24.53 | 1400000
Average | 16761.3333 | 16.7613 | 7.7157 | 8.036 | 170.3333 | 23.8333 | 342 | 41.0667 | 266.9333 | 21.7 | NA | 533.3333 | 0.25333 | 23.75 | 1506666.6667
502.84
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 12760 | 12.76 | 6.65 | 7.71 | 155 | 20 | 272 | 36 | 220 | 16 |  | 400 | 0.2 | 22.29 | 1300000
Max | 19440 | 19.44 | 8.31 | 8.7 | 185 | 28 | 376 | 44 | 335 | 33 |  | 700 | 0.3 | 24.55 | 1700000

## Jhunsi
Jhunsi STP, 16 MLD STP at Prayagraj INLET FLOW & QUALITY REPORT
Date | Daily Feed Quantity MLD (Design- 50 MLD) |  | pH |  | BOD (mg/l) |  | COD (mg/l) |  | TSS (mg/l) |  | FECAL COLIFORM |  | FRC | DEWATERED SLUDGE |  | REMARKS
| M3 | MLD | Inlet pH (Design- <9) | Final pH (Design- 6.5 to 9.0) | Inlet BOD (Design- <250 mg/l) | Final BOD (Design - <20 mg/l) | Inlet COD (Design- <500 mg/l) | Final COD (Design - <50 mg/l) | Inlet TSS (Design- <500 mg/l) | Final TSS (Design - <30 mg/l) | Inlet (Design - NA) | Final (Design - <1000 MPN/100 ml) | Final (Design - 0.2 mg/l) | Outlet Concentration (>20%) | Fecal Coliform (20,00,000 MPN/gTS)
2023-09-01 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | - | From 01.09.2023 to 27.09.2023: Plant is under shutdown due to flood
2023-09-02 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-03 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-04 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-05 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-06 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-07 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-08 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-09 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-10 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-11 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-12 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-13 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-14 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-15 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-16 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-17 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-18 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-19 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-20 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-21 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-22 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-23 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-24 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-25 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-26 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-27 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-28 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | - | From 28.09.2023 to 30.09.2023: 1. Water started receding in river Ganga from 27.09.2023 and most of the I&Ds were free from river water by 28.08.2023.However, pumping from Shastri Bridge SPS is not started as the cleaning of silt & mud deposited in I&Ds, cleaning of choked pipes was in progress. 2. Trivenipuram Nalla is not tapped yet as it is part of Variation related to Jhunsi facility.
2023-09-29 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
2023-09-30 | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
Average | 0 | 0 | - | - | - | - | - | - | - | - | NA | - | - | - | -
0
Source: |  | Logbook of Labarotory at Sewage Treament Plant
Min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
Max | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0